Disabled Toilet Alarm System Specification

| Number: |  |
| --- | --- |
| Issue Number: | 1 |
| Issue Date: | January 2018 |

Contents

1	GENERAL REQUIREMENTS	2

2	STANDARDS AND SPECIFICATIONS	3

3	CONTROL PANEL	4

4	REMOTE DEVICES / OUTSTATIONS	6

5	Toilet Alarm Components	8

6	Assistance Call components	9

7	IP65 rated disabled toilet alarm components	10

8	CABLES	11

9	DOCUMENTATION	12

10	INSTALLATION	13

11	COMMISSIONING	14

12	TRAINING	15

13	MAINTENANCE	16

# GENERAL REQUIREMENTS

  - The contractor shall:

### Be responsible for design, supply, installation, commissioning and maintenance of a radial wired Disabled Toilet Alarm (DTA) system, having an adequate number of competent staff trained and experienced in such and having available a complete set of technical manuals for all equipment installed.

  - All equipment central to the operation of the DTA system (including control and remote devices) shall be fully compliant with  BS 8300:2009+A1:2010 - Design of buildings and their approaches to meet the needs of disabled people – Code of practice

  - All variations from this specification that the contractor proposes to make shall be clearly indicated in writing, making reference to the relevant paragraph(s) of this specification.

# STANDARDS AND SPECIFICATIONS

  - Where applicable the DTA system and installation, shall comply fully with the following British Standard and/or other nominated rules and regulations.

| Standard | Revision | Description |
| --- | --- | --- |
| BS EN 8300:2009 | +A1:2010 | Design of buildings and their approaches to meet the needs of disabled people. |

# CONTROL PANEL

  - General

### The control panel shall:

#### Have the ability to connect up to four disabled toilet alarm or assistance call kits to the unit.

#### Be expandable (daisy chain) in construction to allow for future expansion of the system up to a maximum of 10 units can be connected. Only the first unit shall require power.

#### Each toilet alarm point that is connected shall be clearly identifiable on the front panel with space for individual zone labelling.

#### Each toilet alarm point shall be radially wired to the panel using 2 core cable.

#### The panel shall have four ‘call acknowledge’ buttons and incoming call LEDs – one for each connected toilet alarm or assistance call system.

#### When a call is acknowledged the caller shall be reassured that help is on the way both audibly, by a change of alarm tone and visually, by the flashing of LEDs present on any reset and over door light components.

#### The system shall have a programmable alarm ‘re-sound’ feature which sounds if a call has been acknowledged at the at the control unit but is not reset at the point of the call within a specified time.

#### The unit shall have a separate relay output which shall enable connection to an external beacon. This beacon shall be used to alert staff to the call.

#### The unit shall have an inbuilt power supply and LED to show the system is powered and available for use.

#### The system shall be monitored for short and open circuits and the display will show which toilet alarm or assistance call system is in fault. The system shall also indicate if the fault is open circuit or short circuit.

#### The panel shall fit into a standard UK double gang back box.

#### The unit shall be available in white (RAL 9016) or brushed stainless steel.

  - Control Panel Technical Specification

| Mains Input Voltage | 90-264VAC 47-63Hz |
| --- | --- |
| Mains Current (Max) | 100mA |
| Mains Inrush Current (Max) | 25A |
| Toilet Alarm System Voltage | <24V DC |

# REMOTE DEVICES / OUTSTATIONS

  - General Requirements

### The DTA manufacturer shall have available the following types of remote devices for direct connection to the control panel:

#### 3 part toilet alarm kit

#### Ceiling Pull

#### Over door light

#### Reset point

#### WC door label

#### Call button

#### Call and reset button

#### Wall mount pull cord

#### Call button & 6.35mm jack socket

#### IP65 rated Pull cord

#### IP65 rated Call button

#### IP65 Reset button

#### IP65 rated call and reset button

  - Disabled Toilet Alarm Kit

### The kit shall comprise of the following main components:

#### Pull Switch – ceiling mounted pull cord with fully compliant ‘G’ pulls.

#### Reset Point – reset button and LED to reset calls locally.

#### Light/Sounder – overdoor triangular lens with integral sounder to attract attention.

#### WC sign – vinyl, self-adhesive sign for the toilet door.

### As a minimum each ‘call zone’ shall comprise of an overdoor light, a call point and a re-set point (or an overdoor light and a call/reset point)

### It shall be possible to add additional call, call/reset and reset points to the toilet alarm kits, however only the primary, call, call/reset and reset points shall be monitored for faults.

### Any number of call and reset points can be connected to a single over door light. (Only one overdoor light can be included per toilet alarm kit call zone).

### The kit shall be connected directly to the control panel via 2 core 1.5mm2 (minimum) cable.

### The maximum cable length between the disabled toilet alarm kit and the control panel shall not exceed 500m.

### All components shall be available in a white or stainless steel finish.

### The disabled toilet alarm shall be fully compliant to BS8300:2009.

### As an alternative, it shall be possible to connect an additional ceiling pull – to enable connection of two ceiling pulls to each reset and overdoor light.

### The toilet alarm system shall be powered from the line and not require local power.

### Components shall be available separately enabling a combination of white and stainless steel finish to be fitted.

### When the ceiling mounted cord is pulled, the overdoor light/sounder shall operate. The alarm shall be raised at the control panel, where the call shall be accepted (acknowledged). When the call is accepted the sounder shall change from continuous to cadenced, thus reassuring the caller that help is on the way.

### The kit shall be monitored from the control panel.

### All connections shall be made via rising clamp screw terminals.

# Toilet Alarm Components

  - Ceiling Pull White - The manufacture shall provide a white Ceiling Pull with two red G shaped pulls. It shall be surface mountable and measure 30mm x 80mm diameter.

  - Ceiling Pull Stainless Steel - The manufacture shall provide a stainless steel Ceiling Pull with two red G shaped pulls. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 14mm deep.

  - Over door light white - The manufacture shall provide a white overdoor light with a red triangular lens with integral sounder to attract attention. The sounder shall generate a tone that is at least 90dB @ 30cm. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 58mm deep.

  - Over door light stainless steel - The manufacture shall provide a stainless steel overdoor light with a red triangular lens with integral sounder to attract attention. The sounder shall generate a tone that is at least 90dB @ 30cm. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 60mm deep.

  - Reset point white - The manufacture shall provide a white reset point to allow the user to reset the call. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 13mm deep.

  - Reset point stainless steel - The manufacture shall provide a stainless steel reset point to allow the user to reset the call. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 14mm deep.

# Assistance Call components

  - Call button White - The manufacture shall provide a white call point to allow the user to initiate a call via a button push. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 13mm deep.

  - Call button Stainless Steel - The manufacture shall provide a stainless steel call point to allow the user to initiate a call via a button push. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 13mm deep.

  - Call and reset button White - The manufacture shall provide a white combined call and reset point to allow the user to initiate or reset a call via a button push. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 13mm deep.

  - Call and reset button Stainless Steel - The manufacture shall provide a Stainless Steel combined call and reset point to allow the user to initiate or rest a call via a button push. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 13mm deep.

  - Wall mount pull cord white - The manufacture shall provide a white wall mount pull cord device allow the user to initiate a call via a pull of a red cord which shall have two G pulls. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 13mm deep.

  - Wall mount pull cord stainless steel - The manufacture shall provide a stainless steel wall mount pull cord device to allow the user to initiate a call via a pull of a red cord which shall have two G pulls. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 13mm deep.

  - Call button & 6.35mm jack socket white – The manufacture shall supply a white wall mount call device which has a call button and a 6.35mm jack socket to enable different methods of initiating a call. The jack socket will accept a closing contact input from a pear lead. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 13mm deep.

  - Call button & 6.35mm jack socket stainless steel – The manufacture shall supply a stainless steel wall mount call device which has a call button and a 6.35mm jack socket to enable different methods of initiating a call. The jack socket will accept a closing contact input from a pear lead. It shall be flush mountable using a 25mm deep single gang back box or surface mountable using a ‘round cornered single gang surface box. It shall measure 85mm x 80mm and be 13mm deep.

# IP65 rated disabled toilet alarm components

  - IP65 rated Pull cord - The manufacture shall provide a grey IP65 rated ceiling pull with two red G shaped pulls.

  - IP65 rated Call button - The manufacture shall provide a grey IP65 rated call point to allow the user to initiate a call via a button push.

  - IP65 Reset button - The manufacture shall provide a grey IP65 rated reset point to allow the user to initiate a call via a button push.

  - IP65 rated call and reset button - The manufacture shall provide a grey IP65 rated combined call and reset point to allow the user to initiate or reset a call via a button push.

  - Each IP65 rated unit shall be supplied with a 16mm cable gland to ensure the point of cable entry is suitably sealed

  - All units shall be surface mounting with a grey RAL 7035 finish.

  - Each unit shall measure 80mm W x 80mm H x 60mm D

# CABLES

  - The following cabling guidelines shall be followed:

### 1.5mm security 2-core cable with a screen shall be used.

  - Containment

### Cable support methods must withstand a similar temperature and duration as that of the cable used such that circuit integrity is not reduced and adequate support is maintained.

### Cables should be installed without external joints where possible and other than joints within system components, should be enclosed within junction boxes, labelled ‘DISABED TOILET ALARM SYSTEM’.

### Other than joints within system components terminals used to join cables should be constructed of materials that will withstand a similar temperature and duration to that of the cable.

### Any conduit used should conform to the relevant parts of BS EN 50086.

### Any non metallic trunking used in the system should conform to BS 4678 part 4.

### The preferred colour of the cable shall be red and shall be a single, common colour throughout.

# DOCUMENTATION

  - Tender Documentation

### At the time of tendering, the contractor shall fully and accurately describe the proposed emergency voice communication system and its design concepts.

### The contractor shall provide a complete set of layout drawings and specifications describing all aspects of the system, including:

1.	Detailed component and equipment list with model and manufacturer’s part numbers.

2.	Product sheets for each item of equipment.

3.	Theory of Operations with description of system functions.

4.	Written confirmation that a manufacturer trained representative will provide:

a)	On-site supervision during system installation.

b)	Perform all final testing and commissioning of the installed system.

c)	Instruct operating personnel on all system operations.

### The contractor shall provide a schedule showing the times required to design, build, install, test and commission the system.  The schedule shall also include any special requirements, such as additional training for operating personnel, etc.

  - Contract Documentation

### The contractor shall provide the following set of documents (date for submission of shall be in accordance with the schedule provided by the contractor and as agreed with the client):

| Documentation | Drawings | System Manuals |
| --- | --- | --- |
| System description | System schematic diagram | Master control |
| Checklist of equipment and components | Cabling and wiring diagram | Remote devices |
| Installation instructions | Detailed equipment connection diagrams. | User guides |
| Equipment connection diagrams showing wiring detail of Addressable Device positions with addresses | Building plan loop wiring, location of control/slave panels and remotes. |  |
| Final testing instructions |  |  |
| Commissioning instructions |  |  |
| Certification documents |  |  |
| Log book. |  |  |
| System operating instructions |  |  |
| Routine maintenance instructions and schedules |  |  |

# INSTALLATION

  - General

### The contractor shall install the disabled toilet alarm system in accordance with the documented installation instructions and shall provide all relevant installation documentation.

### The contractor shall be responsible for the correct positioning and fixing of all equipment and components of the system in accordance with previously agreed plans and drawings.

### All cabling and wiring shall be tested before connection to the control and its associated remote devices.

# COMMISSIONING

  - General

### Installation and the commissioning shall be undertaken as a single continuous operation.

### Upon completion of the installation activity, contractor shall Test, Start-up, Commission and Handover the system to the client.

### The contractor shall make use of cable test sheets, installation check report, system layout drawings and system schematic diagrams to record results of commissioning.

  - Testing and Start-up

### The contractor shall:

#### Be responsible for inspection / testing of the complete system.

#### Start up and operate the system for a trial period to ensure correct operation

#### Test all functions in accordance with requirements of design specification and standards.

#### Undertake functionality tests during which the remote devices may be operated.

#### The control panel and associated devices and modules shall be tested in accordance with the guidelines set out in BS 830-9 and manufacturer testing instructions.

  - Commissioning

### Commissioning of the system shall constitute practical completion

### The contractor shall:

#### Demonstrate to the client that the system successfully performs as per the design specification.

#### Provide the client with an agreed quantity of spare parts testing equipment and consumables which are to be used during routine maintenance and testing of the system.

#### Provide a client appointed Disabled Toilet Alarm supervisor with on-site training in the use, operation and maintenance of the system and fire and false alarm procedures.

### The contractor shall present an Acceptance Certificate for signature by the client.

  - Handover

### At the time of handover, the contractor shall provide the client with a copy of the report, component and equipment list, product description sheets, system design specification, system design drawing(s), system schematic diagram(s), system operating and service manuals, certificate of commissioning, users handbook and operating instructions (if this option was provided).

# TRAINING

  - General

### The contractor shall provide the client with details of the training required by personnel to operate and maintain the DISABLED TOILET system.

### The contractor shall provide both System Supervisor Training and other staff training.

### The contractor and the client shall jointly agree the number of staff to attend the training courses.

  - System Supervisor Training

### System supervisor training shall include technical training sessions provided at the contractor’s premises and/or on-site training given during installation and commissioning of the system.

### System supervisor training shall be given by an experienced and competent engineer familiar with the DISABLED TOILET system being installed.

### The scope of training provided shall depend on the type, size and complexity of the system.

### The contractor shall initially provide technical training in all aspects of the system.

  - Other Staff Training

### Other staff training shall include training sessions provided on-site after hand over of the system.

### The training sessions shall be given by an experienced and competent engineer familiar with the fire system installed.

### The scope of training provided shall include full operating instructions in the use of the DISABLED TOILET system.  This shall include instruction in the procedures to be followed in the event of fire and false alarms.

# MAINTENANCE

  - General

### BS 8300:2009+A1:2010 recommends that Disabled Toilet Alarm system systems should be regularly maintained.

### The contractor shall provide detailed information about the maintenance services which can be provided after hand over of the system.

### If requested, the contractor shall prepare and submit a draft maintenance contract for consideration by the client.

### The draft contract shall include complete details of all materials and labour required to maintain the system in correct working order.  It shall also include details of the testing procedures which will be carried out and specify the proposed number of visits per year.

  - System Spares

### The contractor shall provide a detailed list of the system spares which should be kept on-site for maintenance of the system.

### The draft maintenance contract shall also include details of the system spares which are kept on-site for maintenance of the system.

### The contractor shall guarantee the availability of all system spares for a period of not less than ten years.

  - System Test Equipment

### The contractor shall provide a detailed list of the system test equipment and consumables required on-site to maintain the system in perfect working order.

### The draft maintenance contract shall also include details of the system test equipment and consumables which are to be kept on-site for routine maintenance and testing of the system.

Proprietary Notice

All data and information contained within this document is of a proprietary nature with the exclusive title to the same held by Baldwin Boxall Communications Limited. The possession of this document and the use of the information is, therefore, restricted only to those persons duly authorised by Baldwin Boxall Communications Limited. Do not reproduce, transcribe, store in a retrieval system or translate into any language, any part of this document without the prior permission of Baldwin Boxall Communications Limited. In the interest of continual product development, Baldwin Boxall Communications Limited reserves the right to make changes to product specification without notice or liability. Use of Baldwin Boxall Communications Limited products as critical components in life support systems is not authorised except with express written approval from Baldwin Boxall Communications Limited.

TEL: +44 (0)1892 664422
FAX: +44 (0)1892 663146

EMAIL: mail@baldwinboxall.co.uk
WEB: www.baldwinboxall.co.uk

BALDWIN BOXALL COMMUNICATIONS LTD
Wealden Industrial Estate
Farningham Road, Crowborough
East Sussex, TN6 2JR, United Kingdom

L E A D I N G   T H E   W A Y   T O   S A F E T Y