EVC (loop wired) System Specification

| Number: | BB.SD.0006 |
| --- | --- |
| Issue Number: | 1 |
| Issue Date: | March 2015 |

Contents

1	GENERAL REQUIREMENTS	2

2	STANDARDS AND SPECIFICATIONS	3

3	CONTROL PANEL	4

4	REMOTE DEVICES / OUTSTATIONS	7

5	CABLES	12

6	NETWORKING & GRAPHICS	13

7	DOCUMENTATION	14

8	INSTALLATION	15

9	COMMISSIONING	16

10	TRAINING	17

11	MAINTENANCE	18

# GENERAL REQUIREMENTS

  - The contractor shall:

### Be responsible for design, supply, installation, commissioning and maintenance of a loop wired addressable emergency voice communication (EVC) system, having an adequate number of competent staff trained and experienced in such and having available a complete set of technical manuals for all equipment installed.

### Have a minimum of 5 years experience in designing, installing, commissioning and maintaining EVC systems, and be LPS 1014 or BAFE certificated and be approved to BS EN ISO 9001.

### Permit the buyer, or its nominated agent, to conduct a quality audit at the premises where the proposed equipment is manufactured.

  - All equipment central to the operation of the EVC system (including control and remote devices, repeater equipment and power supplies) shall be fully compliant with BS5839 part 9 2011:Fire detection and fire alarm systems for buildings. Code of practice for the design, installation, commissioning and maintenance of emergency voice communication systems.

  - All variations from this specification that the contractor proposes to make shall be clearly indicated in writing, making reference to the relevant paragraph(s) of this specification.

  - The system shall:

### Provide an easy, cost effective upgrade path at end of life, utilising such methods and devices (i.e. existing cabling) so that upgrades can be carried out with minimum downtime.

# STANDARDS AND SPECIFICATIONS

  - Where applicable the emergency voice communication system and installation, shall comply fully with the following British Standards and/or other nominated rules and regulations.

| Standard | Revision | Description |
| --- | --- | --- |
| BS 5839 | BS 5839-1:2013 | Code of practice for system design, installation commissioning and maintenance |
|  | BS 5839-3:1988 | Specification for automatic release mechanisms for certain fire protection equipment. |
|  | BS 5839-6:2004 | Code of practice for the design and installation of fire detection and alarm systems in dwellings. |
|  | BS 5839-8:2013 | Code of practice for the design, installation and servicing of voice alarm systems |
|  | BS 5839-9:2011 | Code of practice for design, installation and maintenance of emergency voice communication systems. |
| BS 4678 | BS 4678-4:1999 | Specification for cable trunking made of insulating material. |
| BS 7846 | BS 7846:2000 | Electric cables. 600/1000V armoured fire resistant cables having thermosetting insulation and low emission of smoke and corrosive gases when affected by fire. |
| BS7671 | BS7671: 2001 | Requirements for electrical installations. IEE Wiring Regulations Sixteenth Edition. |
| BS 7807 | BS 7807 | Code of practice for design, installation and servicing of integrated systems incorporating fire detection and alarm systems and/or other security systems for buildings other than dwellings. |
| HTM05 | HTM05-03 | Fire safety in health care premises. Alarm and detection systems. |
| FIA | FIA | FIA Code of practice for category 1 aspirating detection systems. |
| BS EN 50200 | BS EN 50200 | Method of test for resistance to fire of unprotected small cables for use in emergency circuits. |
| BS EN 50281 | BS EN 50281-1-2:1999 | Electrical apparatus for use in the presence of combustible dust-Selection, installation and maintenance |
| BS EN 60079 | BS EN 60079-14:1997 | Electrical apparatus for explosive gas atmospheres- Electrical installations in hazardous areas (other than mines). |
| BS EN 60702 | BS EN 60702 | Mineral insulated cables and their terminations with a rated voltage not exceeding 750V. |
|  | BS EN 60702-1 | Cables |
|  | BS EN 60702-1 | Terminations |
| BS EN 8300:2009 | +A1:2010 | Design of buildings and their approaches to meet the needs of disabled people. |
| BS EN 9999 |  | Effective fire safety in the design, management and use of buildings |

# CONTROL PANEL

  - General

### The control panel shall:

#### Be modular in construction to allow for future expansion of the system.

#### Incorporate a lockable door to prevent unauthorised use of the manual controls.

#### Be microprocessor based and operate under a multitasking software program.  Operating programs and configuration data must be contained in easily up-datable non-volatile memory (EEPROM). The use of ‘burnt’ EPROMs will not be permitted.

#### Separate processors must be used for the display and control function at each panel.

#### Have the capability to run up to 127 addressable devices with the address code for each held within the addressable device and programmed via a dedicated programming tool.

#### Meet the requirements of BS EN 5839 part 9.

#### Each power output shall be protected by a re-settable fuse rated at 2.5A.

#### Be wall surface or flush mountable and be available in either ‘RAL 7038’ grey or brushed stainless steel finish.

#### It shall be possible to add ‘Slave’ Panels to enable the system to be operated from multiple locations. Slave Panels shall have the facility to be configured to communicate with Remote Units on the system. There must be a Master Control Panel that includes buttons for every Remote Unit on the system.

3.1.1.10	The system shall a ‘self-learn facility’ which auto assigns all remotes sequentially. This feature shall be available for single panelled or networked systems.

  - System Configuration

### The control panel shall:

#### Have the option to be activated in response to an emergency, by a building’s fire detection system (disabled refuge remotes only, all other remote devices shall remain active at all times) and have the facility to be manually overridden to the active state. When in non-active state a short ‘system in standby’ message shall be played if the disabled refuge call button in pressed.

#### Include batteries to provide system power in the event of mains power failure. The batteries shall be housed within the control panel on units of up to 32 way (a separate enclosure for batteries shall be included for larger panels). Battery backup shall be for 24 hours in quiescent mode then three hours at full power.

#### Have an auto commission feature that automatically addresses each remote – it shall also be possible to manually address each remote.

#### Enable local area networking to other controllers and shall be capable of interfacing with third party equipment via a RS232 interface.

#### Prevent opening of the control and indicating equipment without the use of a key.

  - Basic System Functions

### The control panel shall:

#### Monitor the status of all remote devices on the addressable loops.

#### Have a status display which indicates Mains Supply Healthy, Battery High & Low, Charger Fault, Fuse Fault, Common Fault, Processor Fault, Processor Restart, Handset Fault. It shall also feature a lamp test button.

#### Have an independent call button, call status and fault LED for each outstation.

#### It shall be possible to label each button with the location of the remote device.

  - Supervision and Fault Reporting

### The control panel shall:

#### Monitor all critical system components and interconnections (internal and external).  In the event of a failure occurring which prevents correct operation of the alarm functions, a FAULT indicator will illuminate within 100 seconds of occurrence.

#### Monitor the loop for short and open circuit. The loop in case of break shall be bi-directional.

#### Provide short circuit wiring fault isolation to every remote on the loop.

#### Monitor the status of all internal connections and interfaces, including charger, battery and remote signalling functions.

#### Be capable of monitoring and indicating the status of remote units, such as a disabled refuge remote.

#### There shall be an external call output option that causes a pair of contacts to operate after a delay if a call comes in but the handset is not lifted. The delay shall be adjustable from immediate to approximately three minutes.

### Control Panel Technical Specification

| Power supply | 230V AC |
| --- | --- |
| Power consumption | 10VA + 1VA per remote handset connected |
| Weight | 21kg up to 32 way, 26kg up to 64 way unit, 37kg up to 128 way |
| Humidity range | 95% Non-condensing |
| Temperature range | -10˚C to +30˚C |
| Indicators | In-use, call, fault, power, refuge area active, charger and speech volume |
| Remote signalling of fault | Volt-free contact, closing/opening set on commissioning |
| Dimensions mm – W x H x D | 410mm x 290mm x 200 (8-32 way) 410mm x 455mm x 200mm (16-64 way) 410mm x 777mm x 200mm (80-128 way) |
| Bezel Dimensions – W x H x D | 461mm x 340mm x 25mm (8-32 way) 461mm x 506mm x 25mm (16-64 way) |
| Bezel cut out dimensions – W x H | 420mm x 300mm (8-32 way) 420mm x 465mm (16-64 way) |
| Knockouts | 20mm diameter in top and rear |
| Finish | RAL7038 grey or brushed stainless steel |

# REMOTE DEVICES / OUTSTATIONS

  - General Requirements

### The EVC manufacturer shall have available the following types of remote devices for direct connection to the system loops:

- Disabled refuge remote (addressable)

- Advance disabled refuge remote (addressable)

- Fire telephone (addressable)

- Steward telephone (addressable)

- Combined disabled refuge & fire telephone (addressable)

- Disabled toilet alarm

- Loop repeater/interface (addressable when connected to a toilet alarm)

### The remote devices shall be fixed to the installation loop by means of a termination board in back box (not in the disabled toilet alarm kit).

### Addressing of any devices directly connected to the system will be carried out in a manner that does not require manual setting of switches or the use of programming cards.

### Addressable remote device configuration changes shall not prevent a call taking place.

### It shall be possible to connect and mix remote devices on the loop.

### It shall be possible to typically connect 20-30 remotes per loop.

### Each remote device shall be powered from the line so no local power is required

### The unit shall have a system healthy indicator (except the disabled toilet alarm).

  - Disabled Refuge Remotes (Standard)

### Disabled refuge units shall be green in colour or have a brushed stainless steel finish. The stainless steel option shall be provided with separate green signage.

### Each unit shall have an occupied button, which when activated alerts the main control unit.

### Speech shall be speech steered and the occupant will be able to alert the main control panel by simply talking into the unit, once the call button is pushed and the call answered.

### Once the unit has been activated, the main panel shall have the facility to ‘listen in’ to occupied refuge areas – this link must remain open until the remote unit is reset at the control panel.

### The front panel of the remote unit shall have LEDs showing ‘System Healthy’ and ‘Occupied’.

### The unit shall be resettable via the control unit or via the unit’s key switch.

### The backbox shall contain a termination board for ease of installation.

### There shall be a volt free contact, which is active when occupied, to operate overdoor lamps, silence speaker/sounder etc.

### Each unit shall be supplied as surface mountable, with the option to flush mount by using a bezel which shall be available separately.

### Disabled Refuge (Standard) Technical Specification

| Power supply | 12-40V DC self powered from ring circuit |
| --- | --- |
| Power consumption | 30mA @ 35V typical |
| Weight | 1kg |
| Humidity range | 95% non-condensing |
| Temperature range | -10˚C to +40˚C |
| Indicators | System healthy, status |
| Dimensions – W x H x D | 134mm x 134mm x 56mm |
| Bezel dimensions – W x H x D | 154mm x 154mm x 10mm radius |
| Bezel cut out dimensions – W x H | 136mm x 136mm |
| Knockouts | 20mm and 25mm in top and bottom of backbox |
| Unit / Text colour | Green RAL 6024 / RAL white Brushed stainless steel / RAL black |

  - Disabled Refuge Remote (Advance)

### The Advance disabled refuge remote shall be clearly marked Fire Refuge in both Braille and tactile text.

### The unit shall have a green or stainless steel in finish. The stainless steel option shall be provided with separate green signage.

### Each unit shall be supplied as surface mountable, with the option to flush mount by using a bezel which shall be available separately.

### Each unit shall have a built-in induction loop for the hearing impaired.

### The remote units shall have luminescent text for use in areas of low light and tactile text and in Braille script for the visually impaired.

### The front panel of the remote unit shall have a large central vandal resistant call button, (with an illuminated ring) which, when activated, alerts the main control unit.

### Speech shall be speech steered and the occupant will be able to alert the main control panel by simply talking into the unit, once the call button is pushed and the call answered.

### Once the unit has been activated the main panel can ‘listen in’ to refuge areas – this link must remain open until the remote unit is reset either at the control panel or remote device.

### The front panel of the remote unit will have an illuminated ring to indicate ‘System Healthy’ or ‘Occupied’ status.

### The unit shall be resettable via the control unit or via an extended push on the unit’s button.

### The backbox shall contain a termination board for ease of installation.

### There shall be a volt free contact, which is active when occupied, to operate overdoor lamps, silence speaker/sounder etc.

### Disabled Refuge Remote (Advance) Technical Specification

| Power supply | 12-40V DC self powered from ring circuit |
| --- | --- |
| Power consumption (VA) | 30mA @ 35V typical |
| Weight | 3.5kg |
| Humidity range | 95% non-condensing |
| Temperature range | -10˚C to +40˚C |
| Indicators | System healthy, system activated and in-use |
| Dimensions – W x H x D | 180mm x 440mm x 64mm |
| Bezel dimensions – W x H x D | 230mm x 490mm |
| Bezel cut out dimensions – W x H x D | 190mm x 450mm |
| Knockouts | 20mm and 25mm in sides of backbox |
| Unit / Text colour | Green RAL 6024 / RAL white Brushed stainless steel / RAL black |

  - Fire Telephones

### The fire telephone remote shall be clearly marked ‘Fire Telephone’ and offer full duplex communication.

### Fire telephone units shall have the option of either a push door catch or lockable door, with or without beacon.

### The fire telephone remotes shall have a robust red handset with T-Coil and provide a ‘conference call’ facility via the master control panel.

### They shall incorporate a loudspeaker to allow ALL CALL announcements from the Master Control Panel to be heard without the handset being lifted.

### Calls shall be activated when the door of the telephone enclosure is opened.

### Fire telephones shall be red in colour or have a stainless steel finish. The stainless steel option shall have red legend.

### Each unit shall be supplied as surface mountable, with the option to flush mount by using a bezel which shall be available separately.

### Fire Telephone Technical Specification

| Power supply | 12-40V DC |
| --- | --- |
| Power consumption (VA) | 30mA @ 35V typical |
| Weight | 4kg |
| Humidity range | 95% Non-condensing |
| Temperature range | -10˚C to +40˚C |
| Indicators | System Healthy |
| Dimensions mm – W x H x D | 130mm x 350mm x 100mm excluding beacon |
| Bezel Dimensions – W x H x D | 170mm x 390mm x 20mm |
| Bezel cut out dimensions – W x H | 138mm x 358mm |
| Knockouts | 20mm and 25mm |
| Unit / Text colour | Red RAL 2002 / RAL white Brushed stainless steel / RAL 2002 red |

  - Steward Telephones

### The steward telephone remote shall be clearly marked ‘Emergency Telephone’ and offer full duplex communication.

### Steward telephone units shall have the option of either a push door catch or lockable door, with or without beacon.

### The steward telephone shall have a robust red handset with T-Coil and provide a ‘conference call’ facility via the master control panel.

### They shall incorporate a loudspeaker to allow ALL CALL announcements from the Master Control Panel to be heard without the handset being lifted.

### Calls shall be activated when the door of the telephone enclosure is opened.

### Steward telephones shall be green in colour.

### Each unit shall be supplied as surface mountable, with the option to flush mount by using a bezel which shall be available separately.

### Steward Telephone Technical Specification

| Power supply | 12-40V DC |
| --- | --- |
| Power consumption (VA) | 30mA @ 35V typical |
| Weight | 4kg |
| Humidity range | 95% Non-condensing |
| Temperature range | -10˚C to +40˚C |
| Indicators | System Healthy |
| Dimensions mm – W x H x D | 130mm x 350mm x 100mm excluding beacon |
| Bezel Dimensions – W x H x D | 170mm x 390mm x 20mm |
| Bezel cut out dimensions – W x H | 138mm x 358mm |
| Knockouts | 20mm and 25mm |
| Unit / Text colour | Green RAL 6024 / RAL white |

  - Combined Disabled Refuge and Fire Telephone

### The unit shall incorporate a full specification Fire Telephone and Standard Disabled Refuge remote within the same housing.

### The combined unit shall show as one ‘call point’ on the control panel.

### The units shall be either have a red or stainless steel finish or feature a red fire telephone section with a green DRS section.

### Each unit shall be supplied as surface mountable, with the option to flush mount by using a bezel which shall be available separately.

### Combined Fire Telephone/DRS Unit Technical Specification

| Power supply | 12-40V DC |
| --- | --- |
| Power consumption (VA) | 30mA @ 35V typical |
| Weight | 4.5kg |
| Humidity range | 95% Non-condensing |
| Temperature range | -10˚C to +40˚C |
| Indicators | System Healthy and Call Status |
| Dimensions mm – W x H x D | 130mm x 480mm x 100mm excluding beacon |
| Bezel Dimensions – W x H | 170mm x 520mm |
| Bezel cut out dimensions – W x H | 138mm x 486mm |
| Knockouts | 20mm and 25mm in sides of backbox |
| Unit / Text colour | Red RAL 2002 / RAL white Brushed stainless steel / RAL 2002 red Green RAL 6024 / RAL white |

  - Disabled Toilet Alarm Kit

### The kit shall comprise of the following main components:

#### Pull Switch – ceiling mounted pull cord with fully compliant ‘G’ pulls.

#### Reset Point – reset button and LED to reset calls locally.

#### Light/Sounder – overdoor triangular lens with integral sounder to attract attention.

#### WC sign – vinyl, self-adhesive sign for the toilet door.

### The kit shall be connected to the system via a repeater unit.

### All components shall be available in a white or stainless steel finish.

### The disabled toilet alarm shall be fully compliant to BS8300:2009.

### It shall be possible up to two toilet alarm kits to each repeater (and indicated at a single point on the panel).

### As an alternative, it shall be possible to connect an additional ceiling pull – to enable connection of two ceiling pulls to each reset and overdoor light (allowing the ability to use for rooms with two points of call).

### The toilet alarm system shall be powered from the line and not require local power.

### Components shall be available separately enabling a combination of white and stainless steel finish to be fitted.

### When the ceiling mounted cord is pulled, the overdoor light/sounder shall operate. The alarm shall be raised at the control panel, where the call shall be accepted (acknowledged). When the call is accepted the sounder shall change from continuous to cadenced, thus reassuring the caller that help is on the way.

### The kit shall be monitored and have battery backup via the EVC system.

### Plug on terminals to ease installation shall be included.

# CABLES

  - The following cabling guidelines shall be followed:

### Fire resisting 1.5mm enhanced 4-core cable with a screen shall be used for loops.

### Up to 200m cable run between handsets and control panel as standard.

### A ring circuit configuration must be used to wire the remotes.

### A repeater unit must be used if distance between units exceeds 200m.

### It shall be possible to place disabled refuge, fire telephone, combined DRS/fire telephone and toilet alarm units on the same loop.

### It shall be possible to connect 20-30 remotes per loop.

### A repeater unit must be used to connect the toilet alarms to the system.

### Wiring between Master Control Panel and Slave Panel(s) shall require fire resisting 1.5mm enhanced 2 x 4-core cables for each connected ring circuit.

  - BS5839-9:2011: standard fire resisting cables SHALL be considered suitable for:

### EVC systems for use in disabled refuges but not for fire fighting in (a) sprinklered buildings; (b) unsprinklered buildings less than 30m in height, provided that evacuation takes place in three or fewer phases.

### Underground sections of cabling at sports and similar venues.

  - Containment

### Cable support methods must withstand a similar temperature and duration as that of the cable used such that circuit integrity is not reduced and adequate support is maintained.

### Cables should be installed without external joints where possible and other than joints within system components, should be enclosed within junction boxes, labelled ‘EMERGENCY VOICE COMMUNICATION SYSTEM’.

### Other than joints within system components terminals used to join cables should be constructed of materials that will withstand a similar temperature and duration to that of the cable.

### Any conduit used should conform to the relevant parts of BS EN 50086.

### Any non metallic trunking used in the system should conform to BS 4678 part 4.

### The preferred colour of the cable shall be red and shall be a single, common colour throughout.

# NETWORKING & GRAPHICS

  - Networking

### Control and slave consoles shall be wired on a ring circuit.

  - Graphical User Interface

### The system must be designed for use with a touchscreen/mouse (with optional keyboard) and must support connection of a separate monitor.

### The contractor shall be responsible for the installation, commissioning configuration and servicing of a graphical user interface for the EVC system. The manufacturer shall design the GUI layout.

### The graphical user interface software shall:

#### Be designed, written and owned by the company manufacturing the system.

#### Provide the means for annunciation, status display, and control of the EVC system.

#### Support network panels with up to 127 remote devices connected to the system.

#### Provide operator control via mouse, optional keyboard or touch-screen with multimedia compatibility.

#### Display the precise location of events, using a combination of symbols, floor plans, pictures text, audio and video.

#### Store a fault and history log of all events centrally.

#### When an event is registered at any EVC control panel, the graphics system shall display the first screen image for the first activated device.

# DOCUMENTATION

  - Tender Documentation

### At the time of tendering, the contractor shall fully and accurately describe the proposed emergency voice communication system and its design concepts.

### The contractor shall provide a complete set of layout drawings and specifications describing all aspects of the system, including:

1.	Detailed component and equipment list with model and manufacturer’s part numbers.

2.	Product sheets for each item of equipment.

3.	Theory of Operations with description of system functions.

4.	Written confirmation that a manufacturer trained representative will provide:

a)	On-site supervision during system installation.

b)	Perform all final testing and commissioning of the installed system.

c)	Instruct operating personnel on all system operations.

### The contractor shall provide a schedule showing the times required to design, build, install, test and commission the system.  The schedule shall also include any special requirements, such as additional training for operating personnel, etc.

  - Contract Documentation

### The contractor shall provide the following set of documents (date for submission of shall be in accordance with the schedule provided by the contractor and as agreed with the client):

| Documentation | Drawings | System Manuals |
| --- | --- | --- |
| System description | System schematic diagram | Master control |
| Checklist of equipment and components | Cabling and wiring diagram | Remote devices |
| Installation instructions | Detailed equipment connection diagrams. | User guides |
| Equipment connection diagrams showing wiring detail of Addressable Device positions with addresses | Building plan loop wiring, location of control/slave panels and remotes. |  |
| Final testing instructions |  |  |
| Commissioning instructions |  |  |
| Certification documents |  |  |
| Log book. |  |  |
| System operating instructions |  |  |
| Routine maintenance instructions and schedules |  |  |

# INSTALLATION

  - General

### The contractor shall install the EVC system in accordance with the documented installation instructions and shall provide all relevant installation documentation.

### Installation of the system shall be in accordance with the recommendations set out in BS 5839–1:2013 and BS 7671.

### The contractor shall be responsible for the correct positioning and fixing of all equipment and components of the system in accordance with previously agreed plans and drawings.

### All cabling and wiring shall be tested before connection to the control and its associated remote devices.

# COMMISSIONING

  - General

### Installation and the commissioning shall be undertaken as a single continuous operation.

### Upon completion of the installation activity, contractor shall Test, Start-up, Commission and Handover the system to the client.

### The contractor shall make use of cable test sheets, installation check report, system layout drawings and system schematic diagrams to record results of commissioning.

  - Testing and Start-up

### The contractor shall:

#### Be responsible for inspection / testing of the complete system.

#### Start up and operate the system for a trial period to ensure correct operation

#### Test all functions in accordance with requirements of design specification and standards.

#### Undertake functionality tests during which the remote devices may be operated.

#### The control panel and associated devices and modules shall be tested in accordance with the guidelines set out in BS 5839-9 and manufacturer testing instructions.

  - Commissioning

### Commissioning of the system shall constitute practical completion

### The contractor shall:

#### Demonstrate to the client that the system successfully performs as per the design specification.

#### Provide the client with an agreed quantity of spare parts testing equipment and consumables which are to be used during routine maintenance and testing of the system.

#### Provide a client appointed EVC supervisor with on-site training in the use, operation and maintenance of the system and fire and false alarm procedures.

### The contractor shall present an Acceptance Certificate for signature by the client.

  - Handover

### At the time of handover, the contractor shall provide the client with a copy of the report, component and equipment list, product description sheets, system design specification, system design drawing(s), system schematic diagram(s), system operating and service manuals, certificate of commissioning, EVC users handbook and operating instructions (if this option was provided).

# TRAINING

  - General

### The contractor shall provide the client with details of the training required by personnel to operate and maintain the EVC system.

### The contractor shall provide both System Supervisor Training and other staff training.

### The contractor and the client shall jointly agree the number of staff to attend the training courses.

  - System Supervisor Training

### System supervisor training shall include technical training sessions provided at the contractor’s premises and/or on-site training given during installation and commissioning of the system.

### System supervisor training shall be given by an experienced and competent engineer familiar with the EVC system being installed.

### The scope of training provided shall depend on the type, size and complexity of the system.

### The contractor shall initially provide technical training in all aspects of the system.

  - Other Staff Training

### Other staff training shall include training sessions provided on-site after hand over of the system.

### The training sessions shall be given by an experienced and competent engineer familiar with the fire system installed.

### The scope of training provided shall include full operating instructions in the use of the EVC system.  This shall include instruction in the procedures to be followed in the event of fire and false alarms.

# MAINTENANCE

  - General

### BS 5839-9:2011 recommends that EVC systems should be regularly maintained.

### The contractor shall provide detailed information about the maintenance services which can be provided after hand over of the system.

### If requested, the contractor shall prepare and submit a draft maintenance contract for consideration by the client.

### The draft contract shall include complete details of all materials and labour required to maintain the system in correct working order.  It shall also include details of the testing procedures which will be carried out and specify the proposed number of visits per year.

  - System Spares

### The contractor shall provide a detailed list of the system spares which should be kept on-site for maintenance of the system.

### The draft maintenance contract shall also include details of the system spares which are kept on-site for maintenance of the system.

### The contractor shall guarantee the availability of all system spares for a period of not less than ten years.

  - System Test Equipment

### The contractor shall provide a detailed list of the system test equipment and consumables required on-site to maintain the system in perfect working order.

### The draft maintenance contract shall also include details of the system test equipment and consumables which are to be kept on-site for routine maintenance and testing of the system.

Proprietary Notice

All data and information contained within this document is of a proprietary nature with the exclusive title to the same held by Baldwin Boxall Communications Limited. The possession of this document and the use of the information is, therefore, restricted only to those persons duly authorised by Baldwin Boxall Communications Limited. Do not reproduce, transcribe, store in a retrieval system or translate into any language, any part of this document without the prior permission of Baldwin Boxall Communications Limited. In the interest of continual product development, Baldwin Boxall Communications Limited reserves the right to make changes to product specification without notice or liability. Use of Baldwin Boxall Communications Limited products as critical components in life support systems is not authorised except with express written approval from Baldwin Boxall Communications Limited.

TEL: +44 (0)1892 664422
FAX: +44 (0)1892 663146

EMAIL: mail@baldwinboxall.co.uk
WEB: www.baldwinboxall.co.uk

BALDWIN BOXALL COMMUNICATIONS LTD
Wealden Industrial Estate
Farningham Road, Crowborough
East Sussex, TN6 2JR, United Kingdom

L E A D I N G   T H E   W A Y   T O   S A F E T Y