Baldwin Boxall Generic Specification ECLIPSE4 and VIGIL3 amplifiers

Wall mountable Voice Evacuation / Public Address and Sound Amplification Specification

Contents

# Performance Objectives

2. 	Design Parameters

3. 	System Description

4. 	Control Requirements

5. 	System Operation

6. 	System Equipment

7.	Factory Acceptance Test

8. 	System Installation

9. 	System Maintenance

10.	Tests

11.	Documentation

Voice Evacuation / Public Address and Sound Amplification

# Performance Objectives

  - System Description.

    - The wall-mountable Voice Alarm Control and Indicating Equipment (VACIE) shall measure 900mm H x 500mm W x 200mm D.

    - The VACIE shall have full Critical Signal Path monitoring and meet, or even exceed, the stringent standards of BS5839 part 8 and shall be fully EMC compliant.

    - It shall also be third party approved to EN54-4 and EN54-16.

    - The manufacturer shall have full ISO 9001accreditation.

    - The VACIE shall be able to interface to any manufacturers’ Fire Detection equipment. If this link should fail the VA system must operate on a stand-alone basis.

    - The VACIE shall utilise Digital Signal Processing and if this DSP should fail then it shall be possible to make and All Call announcement via Hard Wired Bypass enabled microphones.

    - The VACIE shall have the capacity to house up to four amplifier modules to allow for up to 4 x dual circuits, 4 single circuits or 3 x single circuits with one reserve amplifier.

    - The VACIE and emergency microphones shall have a red VA Active LED which illuminates when an emergency message is broadcast or when an emergency announcement is made.

    - Fault reporting shall be displayed both visually (by means of an amber LED) and audibly by a warning buzzer. It shall be possible to silence this buzzer, however the LED shall remain until the fault has been rectified. Faults to be stored in a history log within the main Voice Alarm matrix.

    - Messages shall be stored in Flash memory within the master unit with a bandwidth of 18KHz and be up to 57 seconds in length. It shall be possible to expand non-critical message length by combining up to three messages. The system shall be able to broadcast all messages simultaneously.  It shall be possible to manually trigger all of these messages via a control microphone. Each VACIE shall be able to store six messages, two of which are the Start and End of test. All messages shall be monitored via an EN54-16 compliant method. It shall be possible to synchronise messages instantly throughout all zones. Messages shall be uploaded and changed via a USB port behind the front panel.

    - The VACIE shall be capable of handling up to 4 outputs and 4 inputs. It shall be possible to monitor up to four dual (A&B) circuits. Each output shall have its own 10 band parametric equalisation (EQ) with audio delay of up to one second and all inputs shall have three band parametric EQ plus bass and treble controls to ensure the best possible intelligibility can be achieved. All inputs shall have programmable prioritisation. The DSP microprocessor shall be able to control each zone and signal path independently.

    - The VACIE shall be able to operate as a centralised system with all the control equipment housed in one location. The system will have capabilities to expand to a decentralised system with 126 routeing matrices by either digital copper or fibre (single or multi-mode) networks.

    - If any zone should fail it will not jeopardise any other zone. The system shall be capable of pulse monitoring (either at 20KHz or 30Hz) of the entire system, including loudspeaker lines and the critical signal path. The Fire Detection equipment shall monitor the Fire Alarm Interface. The Voice Alarm equipment shall indicate the nature of the fault using built in diagnostics, system faults shall also be fed to the Fire Detection equipment.

    - It shall be possible to monitor each loudspeaker line, using end of line monitoring devices.

    - It shall be possible to connect an IP interface to the VACIE that enables remote fault diagnostics. It shall be possible to connect to the interface via internet connected devices to view the status of both the system and network. If the system goes into fault it shall automatically email (up to 6 addresses) with notification of the fault. Via the internet enabled device it shall be possible to view and download all fault and history logs. It shall automatically synchronise all connected router time clocks and users shall have the ability to adjust non-emergency volumes (configured via the router).

    - Configuration of the system shall only be possible by authorised personal. Configuration shall be performed via a laptop connected to an internal USB port and the configuration shall be Pin Number protected.

    - The VACIE shall have space for integral batteries enabling the system to operate for 24 hours in the quiescent state then for a further thirty minutes playing the Evacuate message to all zones if mains power should fail.  Due to the design of certain sized systems an optional battery enclosure may be supplied, this shall be floor mountable (with optional adjustable levelling feet). It shall bolt onto the underside of the VACIE. This battery enclosure shall measure 650mm H x 500mm W x 200mm D. By utilising this battery enclosure it shall be possible to extend the run time in the quiescent state to 72 hours for some system configurations.

      - The VACIE shall contain an EN54-4 approved power supply capable of charging the batteries at up to 8A. The entire system shall run off a non-switchable power supply of 230 Volts.

    - The VACIE shall provide the building with the facilities to broadcast routine and Emergency paging messages to selected or all areas of the building

    - The VACIE shall be able to broadcast a digitally stored voice alarm message to individual or all areas in an emergency situation.

    - The system shall have capabilities to provide background music and advertising announcements throughout the building.

    - To provide everything necessary to provide a fully functioning VA/PA system in accordance with the specification and building requirements.

# The VACIE and speaker installation shall achieve a minimum sound pressure level of 65dB or 10 dB above the typical ambient noise level.

  - Messaging

    - The system shall provide secure, clear and concise instructions to all persons within the building in the event of an emergency to allow evacuation of some or all areas. The messages shall consist of the following:

- Evacuate Message

- Alert Message

- Bomb Alert

- Standard message

- Start of test message

- End of test message

- Design Parameters

  - Provide installations to comply with the requirements of the following standards:

  - BS5839 part 1 2002 & A2 2008 – Fire detection and alarm systems for buildings.

  - BS5839 part 8 2008 – Code of practice for the design, installation and servicing of voice alarm systems.

# BS6259 1997 – Code of practice for planning and installations of sound systems.

# BS9999: 2008 – Code of practice for the fire safety in the design, management and use of buildings.

  - EMC Regulations	55103-1 2009 & 55103-2 2009.

  - EN54 Part 4 - Fire detection and fire alarm systems — power supply equipment.

  - EN54 Part 16 - Fire detection and fire alarm systems – voice alarm control and indicating equipment.

- System Description

  - Project specific, please fill in client’s requirements. Please provide details of the following:

    - Microphones

    - Digital messages

    - Interfaces with other equipment

    - Background music or spot advertisement announcements

    - Networking

    - Loudspeaker zones

    - Loudspeaker design criteria, which includes audibility and intelligibility.

- Control Requirements

  - Provide a wall mountable VACIE consisting of amplification and routeing equipment to be located within the (Consultant to provide this information).

  - Manual announcement facilities are to be provided (Consultant to provide this information).  The manual announcements shall override all other pre-recorded announcements and advertising/background music.

  - The wall mounted enclosure shall be of steel construction.  Sufficient natural and forced ventilation shall be provided to permit continuous operation of the equipment in a room ambient temperature -5 and +40 degrees Celsius. The enclosure shall be IP30 rated.

  - The wall mountable VACIE shall be coated in a textured finish of black colour.  Cable access shall be through the rear and top of the case.  Interconnections shall be by way of removable connectors and not soldered to allow items to be removed for routine maintenance and servicing.  Electrical connections to the unit will be made using DIN rail mounted screw terminal blocks clearly labelled to reference with the interconnection diagrams.

  - If an additional battery box is required it shall be floor standing and mounted to the bottom of the VACIE.

  - Locate VACIE loudspeakers throughout the building wired as monitored circuits.

  - At least two loudspeaker circuits are required in the building. If the building contains an open area of more than 4,000m2 OR if the building is designed to accommodate more than 500 members of the public, dual circuits shall be used. This shall achieve suitable coverage should one of the circuits become short or open circuit.

  - Cabling for the dual circuits shall not be contained within one single sheath.

  - The building shall be divided into evacuation zones in accordance with (Consultant to provide this information).

  - All loudspeaker circuits will be monitored during non broadcast mode with control indication of individual circuits at fault.

  - The monitoring of the system shall include the following:

    - Normal power

    - Standby power

    - Battery chargers

    - Batteries

    - Fuses and protection devices

    - Critical signal paths (definition of a Critical signal paths - all components and interconnections between every fire alarm broadcast initiation point and the input terminals on, or within each loudspeaker enclosure.).

    - Emergency messages

    - Site specific configuration settings.

    - Loudspeaker circuits.

    - Standby amplifiers.

    - All connections to a multi-zone emergency microphone

    - All links between a de-centralised system

    - Detection of missing modules or amplifiers within the critical signal path

    - Automatic level controllers must be monitored and shall fail safe to a pre-determined level, not mute.

  - Provide microphones, fire microphones and/or desk paging control microphones with the following facilities:

    - The broadcast of top priority manual emergency announcements over any combination or all of the evacuation zones.

    - The broadcast of a second priority evacuation tone and message over any combination or all of the evacuation sectors.

  - Provide phased evacuation facilities for the broadcast of various emergency messages throughout the building simultaneously if required.

# The control microphone shall have the facility to provide pre-recorded start of test and end of test messages to all areas.

# The system shall initiate the automatic evacuation procedures upon receipt of a latched command from the fire detection system. The VACIE shall require a de-latch command to reset from the fire detection system.

# Provide from a desk mounting microphone live voice announcements with an automatic chime to all/selected areas.

  - Provide systems to automatically changeover to an integral standby battery supply in the event of mains failure and revert to normal mains supply upon restoration with no loss of broadcast.

  - Depending on amplification requirements it shall be possible to utilise a reserve amplifier to provide backup to maintain the required speech intelligibility in the event of an amplifier failure. Where dual amplifier/circuits are utilised it will not be necessary to use a reserve amplifier as long as the loudspeaker design is in accordance with the BS5839 part 8’s requirements.

- System Operation

  - This information is project specific and needs to be supplied by the consultant.

- System Equipment

  - This information is project specific and needs to be supplied by the consultant.

  - Microphones

    - Touchscreen Control Microphone (TCM)

      - The TCM shall be EN54 part 16 and BS5839 part 8 compliant.

      - The TCM shall be capable of broadcasting to all zones.

      - The TCM shall be connected to a rack installation located (consultant to provide this information)

      - The TCM shall be desk, rack or wall mounted.

      - From the TCM it shall be possible to carry out general paging announcements, either zonal or all call, and select different sources of background music to any zone.

      - From the TCM it shall be possible to carry out emergency live broadcasts at the highest priority.

      - By using a NFC (card or key) and passcode combination, it shall be possible to select and broadcast any of the system’s messages that are stored digitally within the VACIE.

      - If the TCM main processor should fail it shall be possible to undertake an emergency ‘all call’ announcement if the TCM is connected to a system hard wired bypass input.

      - It shall be possible to adjust zone volumes from the TCM.

      - The TCM shall support access control via either Pin or NFC Card

      - Access control shall be used to restrict access to system features

      - The TCM shall have a red ‘VA active’ LED indicator which illuminates during broadcast of an emergency message or emergency live broadcast.

      - It shall be possible to fit an emergency processor bypass ‘all call’ switch.

      - There shall have a seven inch high brightness, capacitive, touchscreen that displays system status and allows the user to interact with the system.

      - All critical signal paths shall be monitored by using the latest available technology and all faults with the system shall be displayed.

      - The microphone shall have the ability to be configured via the screen.

      - It shall be possible to import and export non-emergency messages via a USB Memory Stick.

      - It shall be possible to import and export microphone configuration files via a USB Memory Stick.

      - Fault indicators shall be displayed and all faults stored in a history log.

      - There shall be an activity log which shows all system activity.

      - Connection shall be via RJ45/CAT6 cable.

      - It shall be possible to record non critical messages via the microphone for later broadcast/scheduling.

      - The unit shall have dual output to feed rack A and rack B where dual racks are installed.

      - It shall be possible to connect a third party music audio feed into the microphone that can be routed to any zone or combination of zones.

      - It shall be possible to route additional back ground music sources to all / selected zones.

      - ‘Fault’ and ‘status’ information shall be displayed on the touchscreen and in addition the microphone shall have LED indicators for ‘VA active’, ‘system fault’, ‘general fault’, ‘power on’ and ‘healthy’.

      - The TCM shall be fitted with a sounder to indicate faults; this sounder shall have the ability to be muted

      - The TCM shall have the ability to schedule non-emergency message playback to any or all zones.

      - It shall be possible to configure “Groups” to easily select multiple zones.

    - Voice Alarm Control Microphone

      - The controller will be EN54 part 16 and BS5839 part 8 compliant. It shall be able to control 8, 16, 24, 32, 40, 48, 56 or 64 zones. It shall be possible to rack mount the control microphone with options for up to 80 zones.

      - From the control microphone it will be possible to carry out general paging announcements, either zonal or all call, and select different sources of background music to any zone. By using a key switch it will be possible to select any/all of the system’s messages that are stored digitally within the Voice Alarm router. If the processors contained within the control microphone, fire microphone or routing matrix fail it shall be possible to undertake an emergency ‘all call’ announcement. It shall be possible to adjust zone volume from the control microphone.

      - The microphone shall have a red VA Active LED indicator which illuminates during broadcast of an emergency message or page.

      - It shall be possible to fit an emergency processor bypass ‘all call’ switch.

      - There shall be a three line LED display for each zone select button which will be able to display the zone name, input source and current status of each zone. There shall be an additional LCD display to indicate message choice. It shall show four messages at a time and the user shall be able to scroll through all messages available.

      - All critical signal paths shall be monitored by using the latest available technology and system faults shall be displayed.

      - The microphone shall have the ability to be programmed via a USB connection and will have five programmable function keys.

      - Fault indicators shall include ‘system’, ‘message’, ‘microphone’, ‘processor’ and ‘comms’. Speak now and speech level indicators shall also be a requirement.

      - Connection shall be via RJ45/CAT5.

    - Fire microphones (robust enclosure)

      - The data fire microphone will be EN54 part 16 and BS5839 part 8 compliant. It shall be able to control a single, 4 or 8 zones. From the fire microphone it will be possible to carry out a general emergency announcement either on a zonal or all call basis.

      - All communication to the main control system shall be via RS485.

      - The units shall be housed within a red coloured sealed robust lockable steel enclosure to be wall or flush mountable. It shall also be possible to mount the unit within a 19” rack.

      - All connections to Fire Microphones shall be monitored for open and short circuit conditions.

    - Fire Microphone (mountable within the VACIE)

      - It shall be possible to mount a red ‘all call’ fire microphone within the VACIE front panel. It shall have a push to call button and integral microphone.

    - Paging Microphones

      - Paging microphones shall be aesthetically pleasing and be either desk or wall mountable. They shall be able to control a single zone or 4, 8, 16 or 32 zones. From the paging microphone it will be possible to carry out general announcements either on a zonal or all call basis.

      - Communication with the main control system shall be via an RS485 link with a RJ45 (CAT5 network) cable which will carry both audio and data.

      - 4, 8, 16 and 32 zone paging microphones shall have the option to be fully monitored. The paging microphones shall have the following functions: speak now light, busy light, limiter and zone cancel function. There shall also be ‘data’ and DC indicators to show the unit is functioning correctly.

      - The units shall have capabilities to have optional flip top switches fitted to trigger DVA messages.

  - Telephone Interfaces

    - The manufacturer of the VACIE shall be capable of supplying telephone interfaces to allow an operator to make a paging call from a telephone as follows:

    - Single zone telephone interface complete with an optional chime.

    - Eight zone store and forward telephone interface complete with optional chime.

  - DSP Routeing matrix

    - The VACIE shall contain a DSP Routeing Matrix. It shall be capable of handling 4 audio outputs and 4 audio inputs.

    - It shall be possible to monitor up to four dual (A&B) speaker circuits.

    - It shall be possible to connect up 126 DSP Routing Matrices together in a fault tolerant, fully monitored network.

    - The unit shall be able to mount within the VACIE with the front panel display accessible on the front of the VACIE.

    - The unit shall be fully configurable via a laptop plugged into a USB port housed within the VACIE enclosure.

    - The DSP Routing Matrix shall comply with EN54 part 16 and BS5839 part 8, be fully monitored and be able to provide surveillance at either 30Hz or 20Khz. The system shall provide this surveillance on a pulsed basis. All faults and activity shall be logged.

    - The unit shall have a real time clock which indicates time, day, month and year. This shall be used to date stamp the history log, to trigger night volume reduction and trigger timed messages.

    - The routeing matrix shall have capabilities to control 4 electronically balanced line 0dB audio inputs, 4 electronically balanced 0dBM audio outputs and 8 surveillance inputs.  Each input shall have the following facilities: attenuation, three-band parametric equalisation with bass and treble control with limiter/compressor, chime and high pass filter. The line outputs shall have ten-band parametric EQ with an audio delay of up to one second and attenuation.

    - The routeing matrix shall be able to monitor up to four single zone amplifiers or monitor eight amplifiers for four dual circuits.

    - It shall be possible to utilise a reserve amplifier that shall automatically replace any failed amplifier.

    - The system shall feature inputs for ambient noise sensors. Ambient noise sensors shall be capable of adjusting the system non-emergency volumes to ensure broadcasts can be heard over any background noise.

    - Messages shall be stored on non-volatile flash PROM with a bandwidth of 18kHz, with a frequency response of -3dB at 50Hz and be up to 57 seconds in length. It shall be possible to expand non-critical message length by combining up to three messages. A standalone VACIE system shall be able to broadcast 4 messages simultaneously. It shall be possible to manually trigger all of these messages via a control microphone. The system will be able to store six messages, two of which are the Start and End of test. All messages shall be monitored using the latest compliant technology. It shall be possible to synchronise messages throughout all zones even when two or more routeing matrixes are connected.  It shall be possible to change messages via the USB port mounted within the VACIE enclosure. Messages shall automatically synchronise.

    - The system shall be able to form part of a decentralised system with up to 126 routeing matrices connected via a digital network.

  - Amplifiers

  - The amplifier modules shall be 100 Volt line type and be supplied in the following power rating options: dual 75 Watt, dual 150 Watt, quad 75 Watt, quad 150 Watt and dual 300 Watt. All amplifiers shall have separate input connectors for all inputs.

  - The amplifiers shall be Class D and be at least 90% efficient. The amplifiers shall be able to obtain their rated output power from a nominal 24V battery supply.

  - The amplifiers shall not contain 100V line transformers for efficiency, size and weight requirements.

  - All amplifiers shall incorporate 0dBm balanced line audio inputs.

  - The front panel of each amplifier shall have indicators for amplifier output level and amplifier status (‘over temperature’, ‘over load’, ‘mains connected’ and ‘battery connected’).

  - Up to four amplifier modules shall be housed within the VACIE enclosure.

  - Each amplifier assembly shall contain its own high efficiency switch mode power supply per two amplifier outputs (except dual 300W which shall incorporate one supply per output) with integrated power factor correction.

  - The internal high efficiency switch mode power supplies shall be fully compliant with BS EN54-4:1998 Incorporating Amendments Nos. 1 and 2.

  - Each amplifier module shall be connected to a charger module to supply up to 2A of battery charging current per amplifier up to a total of 4 amplifier modules (total 8A charging current).

  - All fault and status information shall be transmitted to the system.

Dual 75 Watt Amplifier Specification

| 1KHz Rated output power less than 0.2% THD | 75W @ 132 Ohms |
| --- | --- |
| Output regulation | Better than 0.2 dB |
| Output Voltages obtainable | 100V only |
| Frequency response (-3dB) | 35 Hz – 20 kHz |
| Input sensitivity and impedance | 0 dBm @ 10kOhms balanced |
| Input common mode rejection ratio (50Hz – 20kHz) | Better than 40 dB :typically 60 dB |
| Output noise reference to rated output | Better than 80 dB (A) |
| Cross talk between amplifiers at 1Khz | Better than 70dB |
| Supply Voltage (batteries) | 22 – 28V DC |
| Supply current(batteries) standby | 80mA inc surveillance, 60mA without per amplifier |
| Rated output power | 3.75A per amplifier |
| Output stage protection: Thermal Load Action | Output stage above 90 °C Excessive output stage current Reduces input to a safe level using a low distortion VCA |
| Fuse protection AC supply (5 x 20mm) Battery (automotive blade) | 1 x 2A (T) 1 x 20A |
| Terminations: Loudspeaker line output Balanced line inputs DC supply input and paralleling facility | 2 x 2 way cage clamp RJ45 connectors 2 pin crimp connectors |
| Dimensions – mm Weight | W 145 x H 75 x D 310 2.30Kg |
| Mains supply input | IEC 6A filtered connector |
| Mains PSU including power factor correction as part of the amplifier module |  |
| Mains supply | 230 V +10%/-15% 50/60Hz |
| Standby power consumption | 12W |
| Maximum power consumption | 175W |
| Aux DC O/P @ 30V | 2.5A |
| Front panel indicators: Amp status LED Output level LED | AC power, DC power, overload and over temperature 100% yellow / 10% green |

Dual 150 Watt Amplifier Specification

| 1KHz Rated output power less than 0.2% THD | 150W @ 66.6 Ohms |
| --- | --- |
| Output regulation | Better than 0.3 dB |
| Output Voltages obtainable | 100V only |
| Frequency response (-3dB) | 35 Hz – 20 kHz |
| Input sensitivity and impedance | 0dBm @ 10kOhms balanced |
| Input common mode rejection ratio (50Hz – 20kHz) | Better than 40 dB :typically 60 dB |
| Output noise reference to rated output | Better than 80 dB (A) |
| Cross talk between amplifiers at 1Khz | Better than 70dB |
| Supply Voltage (batteries) | 22 – 28V DC |
| Supply current (batteries) standby | 80mA inc surveillance, 60mA without per amplifier |
| Rated output power | 7.5A per amplifier |
| Output stage protection: Thermal Load Action | Output stage above 90 °C Excessive output stage current Reduces input to a safe level using a low distortion VCA |
| Fuse protection AC supply (5 x 20mm) Battery (automotive blade) | 1 x 2A (T) 1 x 20A |
| Terminations: Loudspeaker line output Balanced line inputs DC supply input and paralleling facility | 2 x 2 way cage clamp RJ45 connectors 2 pin crimp connectors |
| Dimensions – mm Weight | W 145 x H 75 x D 310 2.30Kg |
| Mains supply input | IEC 6A filtered connector |
| Mains PSU including power factor correction as part of the amplifier module |  |
| Mains supply | 230 V +10%/-15% 50/60Hz |
| Standby power consumption | 12W |
| Maximum power consumption | 350W |
| Aux DC O/P @ 30V | 2.5A |
| Front panel indicators: Amp status LED Output level LED | AC power, DC power, overload and over temperature 100% yellow / 10% green |

Quad 75 Watt Amplifier Specification

| 1KHz Rated output power less than 0.2% THD | 75W @ 132 Ohms |
| --- | --- |
| Output regulation | Better than 0.2 dB |
| Output Voltages obtainable | 100V only |
| Frequency response (-3dB) | 35 Hz – 20 kHz |
| Input sensitivity and impedance | 0dBm @ 10kOhms balanced |
| Input common mode rejection ratio (50Hz – 20kHz) | Better than 40 dB :typically 60 dB |
| Output noise reference to rated output | Better than 80 dB (A) |
| Cross talk between amplifiers at 1Khz | Better than 70dB |
| Supply Voltage (batteries) | 22 – 28V DC |
| Supply current (batteries) standby | 80mA inc surveillance, 60mA without per amplifier |
| Rated output power | 3.75A per amplifier |
| Output stage protection: Thermal Load Action | Output stage above 90 °C Excessive output stage current Reduces input to a safe level using a low distortion VCA |
| Fuse protection AC supply (5 x 20mm) Battery (automotive blade) | 2 x 2A (T) 2 x 20A |
| Terminations: Loudspeaker line output Balanced line inputs DC supply input and paralleling facility | 4 x 2 way cage clamp RJ45 connectors 2 pin crimp connectors |
| Dimensions – mm Weight | W 145 x H 75 x D 310 3.1Kg |
| Mains supply input | IEC 6A filtered connector |
| Mains PSU including power factor correction as part of the amplifier module |  |
| Mains supply | 230 V +10%/-15% 50/60Hz |
| Standby power consumption | 24W |
| Maximum power consumption | 350W |
| Aux DC O/P @ 30V | 5A |
| Front panel indicators: Amp status LED Output level LED | AC power, DC power, overload and over temperature 100% yellow / 10% green |

Quad 150 Watt Amplifier Specification

| 1KHz Rated output power less than 0.2% THD | 150W @ 66 Ohms |
| --- | --- |
| Output regulation | Better than 0.3 dB |
| Output Voltages obtainable | 100V only |
| Frequency response (-3dB) | 35 Hz – 20 kHz |
| Input sensitivity and impedance | 0dBm @ 10kOhms balanced |
| Input common mode rejection ratio (50Hz – 20kHz) | Better than 40 dB :typically 60 dB |
| Output noise reference to rated output | Better than 80 dB (A) |
| Cross talk between amplifiers at 1Khz | Better than 70dB |
| Supply Voltage (batteries) | 22 – 28V DC |
| Supply current (batteries) standby | 80mA inc surveillance, 60mA without per amplifier |
| Rated output power | 7.5A per amplifier |
| Output stage protection: Thermal Load Action | Output stage above 90 °C Excessive output stage current Reduces input to a safe level using a low distortion VCA |
| Fuse protection AC supply (5 x 20mm) Battery (automotive blade) | 2 x 2A (T) 2 x 20A |
| Terminations: Loudspeaker line output Balanced line inputs DC supply input and paralleling facility | 4 x 2 way cage clamp RJ45 connectors 2 pin crimp connectors |
| Dimensions – mm Weight | W 145 x H 75 x D 310 3.1Kg |
| Mains supply input | IEC 6A filtered connector |
| Mains PSU including power factor correction as part of the amplifier module |  |
| Mains supply | 230 V +10%/-15% 50/60Hz |
| Standby power consumption | 24W |
| Maximum power consumption | 700W |
| Aux DC O/P @ 30V | 5A |
| Front panel indicators: Amp status LED Output level LED | AC power, DC power, overload and over temperature 100% yellow / 10% green |

Dual 300 Watt Amplifier Specification

| 1KHz Rated output power less than 0.2% THD | 300W @ 33.3 Ohms |
| --- | --- |
| Output regulation | Better than 0.5 dB |
| Output Voltages obtainable | 100V only |
| Frequency response (-3dB) | 35 Hz – 20 kHz |
| Input sensitivity and impedance | 0dBm @ 10kOhms balanced |
| Input common mode rejection ratio (50Hz – 20kHz) | Better than 40 dB :typically 60 dB |
| Output noise reference to rated output | Better than 85 dB (A) |
| Cross talk between amplifiers at 1Khz | Better than 70dB |
| Supply Voltage (batteries) | 22 – 28V DC |
| Supply current (batteries) standby | 160mA with surveillance, 120mA without per amplifier |
| Rated output power | 14A per amplifier |
| Output stage protection: Thermal Load Action | Output stage above 90 °C Excessive output stage current Reduces input to a safe level using a low distortion VCA |
| Fuse protection AC supply (5 x 20mm) Battery (automotive blade) | 2 x 2A (T) 2 x 20A |
| Terminations: Loudspeaker line output Balanced line inputs DC supply input and paralleling facility | 2 x 2 way cage clamp RJ45 connectors 2 pin crimp connectors |
| Dimensions – mm Weight | W 145 x H 75 x D 310 3.1Kg |
| Mains supply input | IEC 6A filtered connector |
| Mains PSU including power factor correction as part of the amplifier module |  |
| Mains supply | 230 V +10%/-15% 50/60Hz |
| Standby power consumption | 24W |
| Maximum power consumption | 700W |
| Aux DC O/P @ 30V | 5A |
| Front panel indicators: Amp status LED Output level LED | AC power, DC power, overload and over temperature 100% yellow / 10% green |

## Charger Module

### The charger shall be fitted within the VACIE enclosure.

### It shall be possible to connect up to four amplifiers to a charger module to give a total battery charging current of 8A.

### The charger module shall provide (with associated sealed lead acid batteries) a minimum of 24 hours of system operation in the quiescent condition followed by 30 minutes at full load.

### The charger module shall be fully compliant with BS EN54-4:1998 Incorporating Amendments Nos. 1 and 2

### The charger module shall be capable of charging a battery discharged to its final voltage to at least 80% of its rated capacity within 24 hours and to its rated capacity within a further 48 hours.

### The power supply in the battery charger is to have a constant voltage output with compensation for variation in battery temperature.

### The charger module shall protect the batteries from over discharge.

### The charger module shall maintain the batteries at float level and in good condition at an ambient temperatures between -5 and 40 degrees Celsius.

### The charger module shall supply fault and status information to the rest of the system.

### Provide visual indication of mains status, battery disconnected and charger fail on the power supply module should be indicated as well as on the routeing matrix.

Charger module specification

| Voltage @ 20°C | 27.3V |
| --- | --- |
| Temperature compensation | -48m V/°C |
| Maximum current | 10A |
| Battery low fault voltage | 22V |
| Battery high resistance fault | 22m Ohm |
| Battery deep discharge cut off voltage | 18V |
| Volt free fault relay output contacts | 100V @ 1A maximum |
| Front panel indicators |  |
| AC supply | AC supply ‘on’ |
| OK | No fault |
| Fuse | Fuse fault |
| Charger fault | Charger fault |
| High resistance battery | High resistance battery fault |
| Low | Battery voltage low fault |
| Terminations |  |
| 24V battery input | 2 pin screw connector |
| DC output, fault relay contacts and external temperature sensor connection | 8 pin screw connector |
| DC & Data | 5 x RJ45 connectors |

- Digital Network

  - It shall be possible for the VACIE to form part of a decentralised system and systems shall be linked via a digital network. Cabling between systems shall be as either copper, fibre or both. In each of the DSP Routing Matrices there shall be fitted a network control card that communicates to the VACIE mounted copper or fibre (Single or Multi-Mode) interface modules.

  - The copper or fibre network shall be connected in a loop configuration to minimise cabling. The system must continue to function if cabling is damaged in a single location.

  - It shall be possible to support up to 14 concurrent audio channels and two RS485 control channels.

  - Network status indicators are to be provided and the network fully monitored.

  - There shall be an optional system reset feature.

  - Network Control Card

      - It shall be possible to configure the network control cards via a laptop connected to the VACIE’s internally mounted USB port.

      - The following connectors shall be provided: optional system reset feature (two pin); connector for clockwise network cable (CAT5 patch lead); connector for anti-clockwise network cable (CAT5 patch lead).

      - Slow speed option shall provide 6 concurrent audio channels with 2xRS485 channels. Fast speed option shall provide 14 concurrent audio channels with 2xRS485 channels.

      - The RS485 channels shall be independently configurable for speed, stop bits and parity.

    - Digital Network Copper Interface

      - It shall be possible to connect the copper interface to the network control card by CAT5 patch lead, for connection clockwise or anti-clockwise.

      - The copper interface module shall have screw terminals for two transmit conductors (twisted pair recommended). It shall also have screw terminals for two receive conductors (twisted pair recommended) and a screw terminal for ground.

      - It shall be possible to transmit slow speed up to a distance of 300m, or fast speed up to a distance of 200m.

    - Digital Network Fibre Interface – multi mode

      - It shall be possible to connect the multi-mode fibre interface to the network control card by CAT5 patch lead, for connection clockwise or anti-clockwise.

      - The fibre interface module shall have an ST fibre transmit connector (multi-mode) and a ST fibre receive connector (multi-mode). There shall also be a screw terminal for ground.

      - Fibre types supported shall be OM1 (62.5/125), OM2 (50/125) and OM3 (50/125)

      - It shall be possible to transmit at either slow or fast speed at a distance up to 3km (OM1), 2km (OM2) and 2km (OM3).

    - Digital Network Fibre Interface – single mode

      - It shall be possible to connect the single-mode fibre interface to the network control card by CAT5 patch lead, for connection clockwise or anti-clockwise.

      - The fibre interface module shall have an ST fibre transmit connector (single-mode) and a ST fibre receive connector (single-mode). There shall also be a screw terminal for ground.

      - Fibre types supported shall be OS1 (9/125) and OS2 (9/125)

      - It shall be possible to transmit at either slow or fast speed at a distance up to 4km.

  - Ambient Noise Sensing (optional)

    - This facility is ideal for any location where Speech intelligibility could be a problem due to variable noise level, such as Leisure centres, railway stations, shopping malls or factories etc. When the area is at its quietest the volume of the announcements or music will reduce. When the areas are at their busiest and noisiest the amplifiers increase in power to ensure that all announcements etc. will be audible above the background noise.

    - The Ambient Noise Sensing device shall work in conjunction with DSP routeing matrix to automatically adjust the power of the amplifier depending on the ambient noise.

    - The Ambient noise sensor shall contain a dynamic microphone capsule, the output of which shall be amplified then converted to produce a variable current output.

    - The amplifier that is used to convert the signal shall have band pass filters to ensure the system only responds to noise that affects the level of ambient noise.

  - Background music

    - The system shall have capabilities to play up to four different music sources to any zone. (consultant - please provide further information on this)

  - Room panels – type 1 – volume control & channel source select

    - It shall be possible to locally control audio facilities via room panels. The finish of the panel shall be stainless steel. The room panel should have the option to be mounted within a protective stainless steel enclosure. The room panel shall enable channel select and volume adjustment to the local zone. (Consultant to provide further information on this.)

  - Room panels – type 2 – audio input panel with volume control

    - It shall be possible to locally control audio facilities via room panels. The finish of the panel shall be stainless steel. The room panel should have the option to be mounted within a protective stainless steel enclosure. The panel shall provide facilities to connect a music source and/or microphone for local broadcast. The panel shall have two phono sockets and 35mm jack socket for input from music source. The panel shall have switches for: on/off priority for microphone and auto fade switch. (Consultant to provide further information on this.)

  - Advert injection

    - The system shall have sufficient inputs to allow for a single advert injection machine. . (consultant - please provide further information on this)

  - Fire Alarm Interface

    - The system shall have a fire alarm interface to allow triggering from the Fire Detection system. (consultant - please provide further information on this)

  - Interfaces to other equipment

  - The system shall allow for inputs from other equipment (consultant - please provide further information on this)

  - Touchscreen

    - The system shall have capabilities to be controlled be Touchscreen software.

  - Download software

    - The system shall have capabilities to be programmed via laptop computer via the VACIE internally mounted USB socket.

  - Remote access and monitoring

    - The system shall have capabilities to allow remote access and monitoring of the system.

  - Loudspeakers

    - The loudspeaker design is the responsibility of the sound system contractor unless otherwise agreed.

    - The supplied loudspeakers shall be compliant with BS5839 part 8 and EN54 part 24.

  - Recommended loudspeakers:

    - HORN – for use in external and industrial environments or environments with high noise levels or in acoustically difficult conditions.

    - FLUSH MOUNTING – for use in offices, department stores and supermarkets.

    - Wall mounted – for use in offices, small workshops, stores and general small areas in buildings.

    - Bi-directional – for use in corridors and long narrow areas.

    - Column having a wide horizontal and narrow vertical coverage angle – for use in halls and concourse areas.

    - PROJECTOR – mounted in a tube fixed by means of an adjustable bracket thus enabling the propagation of sound in a preferred direction.

    - EXPLOSION-PROTECTED (for example flameproof horn) – suitable for use in potentially explosive areas.

- Factory Acceptance Test

  - The manufacturer shall provide a detailed Factory Acceptance Test to be held at their premises.

- System installation

  - The installation of the system is to be carried out by others and the manufacturer of the system shall provide detailed wiring diagrams and operating manuals.

- System Maintenance

  - The manufacturer of the Voice Evacuation system shall be able to maintain the system on a quarterly basis. Maintenance to be carried out must include.

  - Daily – To be completed by the end user

    - The following routine maintenance is to be carried out by a competent person as appointed by the customer.  Baldwin Boxall will allow one hour for refresher training of staff during the annual visit.

    - Check control panel indicators are operating as normal and complete daily log. Report any faults.

    - Check fault records to confirm any outstanding actions.

  - Weekly –  To be completed by the end user

    - The following routine maintenance is to be carried out by a competent person as appointed by the customer.  Baldwin Boxall will allow one hour for refresher training of staff during the annual visit.

    - Test system functionality in conjunction with Fire Alarm System, make subjective assessment of message intelligibility.

    - Test all microphones for correct operation.

    - At least one loudspeaker must be checked weekly, over a 13 week period all loudspeaker zones must be checked.

    - Report and log any faults identified. Complete system test log.

  - Quarterly –  To be carried out by the manufacturer

    - Scheduled attendance by maintenance engineer to carry out inspection of systems.  As a minimum, the following will be checked during the visit:

    - Visual check of batteries and battery connections and electrically test to determine any deterioration.

    - Test Emergency messages and Fire Microphones.

    - Check and record parameters of ‘end line monitors’.

    - Make subjective assessment of message intelligibility and general condition of speakers.

    - Check and test interface connections with premise’s Fire Alarm Panel.

    - Carry out functionality test of system.

    - Review report log and identify/address any outstanding events.

    - Provide refresher training for site appointed staff (six monthlies).

    - Discharge test of battery system.

  - Annually –  To be carried out by the manufacturer

    - Scheduled attendance by maintenance Engineer to carry out inspection of systems and provide Certificate of Compliance to BS5839 Part 8.

    - In addition to those items identified in the quarterly test, the following will be carried out:

    - Visual check of systems and infrastructure wiring.

    - Check the Sound Pressure Level at each loudspeaker zone; confirm that the Emergency Broadcast is at a practical level above the ambient noise.  RASTI tests are not included, we would be pleased to provide quotations for this service.

    - Assess results against previously reported figures, to determine overall system performance.

    - Issue Certificate of Compliance to BS5839 Part 8.

- Tests

# Documentation

  - Issue a system test certificate detailing compliance will the relevant British Standards and this specification.

  - Issue copies of all documentation immediately to the engineer for comment prior to inclusion in the handover documentation.