Baldwin Boxall Generic Specification Utilising VIGIL EVAS

Voice Evacuation / Public Address and Sound Amplification Specification

Contents

# 1. 	Performance Objectives

2. 	Design Parameters

3. 	System Description

4. 	Control Requirements

5. 	System Operation

6. 	System Equipment

7.	Factory Acceptance Test

8. 	System Installation

9. 	System Maintenance

10.	Tests

11.	Documentation

Voice Evacuation / Public Address and Sound Amplification

# Performance Objectives

  - System Description.

    - The Voice Alarm (VACIE) system shall have full Critical Signal Path monitoring and meet, or even exceed, the stringent standards of BS5839 part 8 and shall be fully EMC compliant. The product shall have undergone third party testing to EN54 part 16. Third party certification to BSEN54 shall be available upon request. The manufacturer shall have full ISO 9001/2008 accreditation. The VA equipment must be able to latch to any manufacturers’ Fire Detection equipment. If this link should fail the VA system must operate on a stand-alone basis. The equipment shall utilise Digital Signal Processing control and if this DSP should fail then it is a necessity that the DSP is overridden and an ‘all call’ announcement shall be made from the main control microphone. The system shall have another emergency override should the DSP fail (two inputs in total). The system must not utilise any rotary discs (i.e. computer hard disc) or any other media moving parts.

    - The voice alarm routing matrix and control microphones shall have a red LED which illuminates when the evacuate message is broadcast.

    - Fault reporting shall be displayed both visually (by means of an amber LED) and aurally by a warning buzzer. It shall be possible to silence this buzzer, however the LED shall remain until the fault has been rectified. Faults to be stored in a history log within the main Voice Alarm matrix.

    - Messages shall be stored Flash memory within the master unit with a bandwidth of 18KHz and be up to 57 seconds in length. It shall be possible to expand non-critical message length by combining up to three messages. The system shall be able to broadcast all messages simultaneously.  It shall be possible to manually trigger all of these messages via a control microphone. The system will be able to store six messages, two of which are the Start and End of test. All messages shall be monitored using the ‘watch dog’ method. It shall be possible to synchronise messages instantly throughout all zones. Messages can be changed via the front panel USB2 port.

    - The unit shall have a non volatile EPROM processor bypass emergency message, which is used if the DSP fails during an emergency message.

    - The Voice Alarm master unit shall be capable of handling 7 outputs, all these being dual circuit with 8 inputs. Each output shall have its own 10 band parametric equalisation with audio delay of up to one second and all inputs shall have three band parametric EQ plus bass and treble equalisation to ensure maximum sound quality. All inputs shall have programmable prioritisation. The DSP microprocessor shall be able to control each zone and signal path independently.

    - The Voice Alarm shall be able to operate as a centralised system with all the control equipment housed in one location. The system will have capabilities to expand to a decentralised system with 126 routeing matrices by either digital copper or fibre networks.

    - If any zone should fail it will not jeopardise any other zone. The system shall be capable of either pulse or continuous monitoring (either at 20KHz or 30Hz) of the entire system, including loudspeaker lines and the critical signal path. The Fire Detection equipment shall monitor the Fire Alarm Interface. The Voice Alarm equipment shall indicate the nature of the fault using built in diagnostics, system faults shall also be fed to the Fire Detection equipment.

    - It shall be possible to monitor each loudspeaker line, using end of line monitoring devices.  Each zone shall be dual circuit and loudspeaker lines shall be interleaved. This depends on specific site requirements and specification. The manufacturer shall also have a dc line monitoring option available (see paragraph 1.1.10 for further information).

    - The dc line monitoring shall enable dual loudspeaker circuits to connect to a single amplifier. Failure of either the A or B circuit from one amplifier will not affect the other circuit. Please note, using this technology, it is necessary to fit capacitors to individual 100V loudspeakers.

    - It shall be possible to connect a din rail interface to the voice evacuation system via an IP network that enables remote fault diagnostics. It shall be possible to connect to the interface via internet connected devices to view the status of both the system and network. If the system goes into fault it shall automatically email (up to 6 addresses) with notification of the fault. Via the internet enabled device it shall be possible to view and download all fault and history logs. It shall automatically synchronise all connected router time clocks and users shall have the ability to adjust non-emergency volumes (configured via the router).

    - The ability to configure and program the system shall not be accessible by end users, to do this the system must use a key operated switch with program access codes to allow the engineer access to four various levels. The system shall also be programmable from a laptop PC via a front panel USB2 port.

    - The system shall be battery backed in case of power failure and should be able to run for 24 hours (expandable to 72 hours) in quiescent mode then for a further thirty minutes on full power. The system will contain power supply chargers, which provide power to the amplifiers and supply an up to 10A charge to the batteries. The entire system shall run off a non-switchable power supply of 230 Volts.

    - The voice evacuation system (VACIE) shall provide the building with the facilities to broadcast routine paging messages to selected areas of the building and to provide a digitally stored voice alarm message to all areas in an emergency situation.  The system shall conform to EN54 part 16, BS5839 Part 8 and also be fully compliant with EMC regulations.

  - Messaging

    - The system shall provide secure, clear and concise instructions to all persons within the building in the event of an emergency to allow evacuation of all areas. The messages shall consist of the following:

- Evacuate Message

- Alert Message

- Bomb Alert

- Standard message

- Start of test message

- End of test message

  - Provide public address announcements throughout the building.

  - The system shall have capabilities to provide background music and advertising announcements throughout the building.

  - To provide everything necessary to provide a fully functioning VA/PA system in accordance with the specification and building requirements.

  - The manufacturer shall be accredited to ISO9001:2015.

- Design Parameters

  - Provide installations to comply with the requirements of the following standards:

    - EN54 part 16 – Fire alarm and fire alarm systems. Voice alarm control and indicating equipment.

    - EN54 part 4 – Fire alarm and fire alarm systems power supply equipment.

    - BS5839 part 1 2002 & A2 2008 – Fire detection and alarm systems for buildings.

    - BS5839 part 8 2008 – Code of practice for the design, installation and servicing of voice alarm systems.

# BS5839 part 9 2003 – Code of practice for emergency voice communication systems.

# BS6259 1997 – Code of practice for planning and installations of sound systems.

# BS9999: 2008 – Code of practice for the fire safety in the design, management and use of buildings.

    - (EMC) Directive 2014/30/EU

# The Voice Evacuation System (VACIE) shall achieve a minimum sound pressure level of 65dB or 10 dB above the typical ambient noise level.

- System Description

  - Project specific, please fill in client’s requirements. Please provide details of the following:

    - Microphones

    - Digital messages

    - Interfaces with other equipment

    - Background music or spot advertisement announcements

    - Networking

    - Loudspeaker zones

    - Loudspeaker design criteria, which includes audibility and intelligibility.

- Control Requirements

  - Provide a VACIE consisting of amplification and routeing equipment to be located within (Consultant to provide this information).

  - Manual announcement facilities are to be provided (Consultant to provide this information).  The manual announcements shall override all other pre-recorded announcements and advertising/background music.

  - The central control equipment shall be located within (Consultant to provide this information – please note that the VACIE can either be centralised or decentralised depending building requirements).

    - Equipment will be housed within high quality 19 inch racks and which will interface with the fire alarm detection control panels via a monitored link. This link is to be monitored by the fire detection panel. A standard 19 inch rack or racks shall be provided to accommodate the central equipment.

    - The rack shall be of steel construction or feature aluminium frames with steel panels.  Sufficient natural ventilation shall be provided to permit continuous operation of the equipment in a room ambient temperature 0 and +30 degrees Celsius.

    - Equipment shall be installed in the rack in logical (signal path) sequence.  Notwithstanding this, equipment requiring routine operation (switch panels, etc.) shall be at a convenient working height.  Unused rack space shall be filled with blank panels.

    - Internal power distribution panels shall be provided.  The mains distribution shall be via a front mounted panel fitted with independent circuit breakers and soft start operation.  Complete with IEC leads for connection purposes.

    - Racks shall be coated in a textured finish of neutral colour and fitted with a lockable glazed front door.  The rear door shall be steel and shall be removable to provide access to the rear of the equipment.  All equipment will be removable from the front of the rack.  Interconnections shall be by way of removable connectors and not soldered to allow items to be removed for routine maintenance and servicing.  Electrical connections to the rack will be made using DIN rail mounted screw terminal blocks clearly labelled to reference with the interconnection diagrams.

  - Locate VACIE loudspeakers throughout the building wired as monitored circuits.

  - At least two loudspeaker circuits are required in the building. If the building contains an open area of more than 4,000m2 OR if the building is designed to accommodate more than 500 members of the public, dual circuits shall be used. This achieves suitable coverage should one of the circuits become short or open circuit.

  - Cabling for the dual circuits shall not be contained within one single sheath.

  - The building shall be divided into evacuation zones in accordance with (Consultant to provide this information).

  - All loudspeaker circuits will be under constant automatic surveillance during non broadcast mode with control indication of individual circuits at fault.

  - The monitoring of the system shall include the following:

    - Normal power

    - Standby power

    - Battery chargers

    - Fuses and protection devices

    - Critical signal paths (definition of a Critical signal paths ~ all components and interconnections between every fire alarm broadcast initiation point and the input terminals on, or within each loudspeaker enclosure.).

    - Emergency messages

    - Loudspeaker circuits

    - Standby amplifiers.

    - Select wires on a multi-zone emergency microphone

    - All links between a de-centralised system

    - Detection of missing modules or amplifiers within the critical signal path

    - Automatic level controllers must be monitored and shall fail safe to a pre-determined level, not mute.

  - Provide microphones, Fire microphones and/or desk paging control microphones with the following facilities:

    - The broadcast of top priority manual emergency announcements over any combination or all of the evacuation sectors.

    - The broadcast of a second priority evacuation tone and message over any combination or all of the evacuation sectors.

  - Provide phased evacuation facilities for the broadcast of various emergency messages throughout the building simultaneously if required.

# The control microphone shall have the facility to provide pre-recorded start of test and end of test messages to all areas.

# The system shall initiate the automatic evacuation procedures upon receipt of a latched command from the fire detection system. The VACIE shall require a de-latch command to reset from the fire detection system.

# Provide from a desk mounting microphone live voice announcements with an automatic chime to all/various areas.

  - Store each pre-recorded tone/announcement message on flash and monitor.

  - Provide systems to automatically changeover to an integral standby battery supply in the event of mains failure and revert to normal mains supply upon restoration with no loss of broadcast.

  - A reserve amplifier shall be used to provide backup to maintain the required speech intelligibility in the event of an amplifier failure. Where dual amplifier/circuits are utilised it will not be necessary to use a reserve amplifier as long as the loudspeaker design is in accordance with the BS5839 part 8’s requirements.

- System Operation

  - This information is project specific and needs to be supplied by the consultant.

- System Equipment

  - Touchscreen Control Microphone (TCM)

### The TCM shall be the central fault reporting device for the voice evacuation system; therefore one must be present for every EN54 installation.

### The TCM shall be connected to a rack installation located AIM.

### The TCM shall be able to control up to a maximum of 800 zones.

### The TCM shall be desk, rack or wall mounted.

### From the TCM it shall be possible to carry out general paging announcements, either zonal or all call, and select different sources of background music to any zone.

### From the TCM it shall be possible to carry out emergency live broadcasts at the highest priority.

### By using a NFC (card or key) and passcode combination, it shall be possible to select and broadcast any of the system’s messages that are stored digitally within the AOMs.

### If the TCM main processor should fail it shall be possible to undertake an emergency ‘all call’ announcement if the TCM is connected to an AOM hard wired bypass input.

### It shall be possible to adjust zone volume from the TCM.

### The TCM shall support access control via either Pin or NFC Card

### Access control shall be used to restrict access to system features

### The TCM shall have a red ‘VA active’ LED indicator which illuminates during broadcast of an emergency message or emergency live broadcast.

### It shall be possible to fit an emergency processor bypass ‘all call’ switch.

### There shall have a seven inch high brightness, capacitive, touchscreen that displays system status and allows the user to interact with the system.

### All critical signal paths shall be monitored by using the latest available technology and all faults with the system shall be displayed.

### The microphone shall have the ability to be programmed via the screen.

### Fault indicators shall be displayed and all faults stored in a history log.

### There shall be an activity log which shows all system activity.

### Connection shall be via RJ45/CAT5.

### It shall be possible to record non critical messages via the microphone for later broadcast/scheduling.

### The unit shall have dual output to feed rack A and rack B where dual racks are installed.

### It shall be possible to connect a third party music audio source to the microphone that can be routed to any zone or combination of zones.

### ‘Fault’ and ‘status’ information shall be displayed on the touchscreen and in addition the microphone shall have LED indicators for ‘VA active’, ‘system fault’, ‘general fault’, ‘power on’ and ‘healthy’.

### The TCM shall be fitted with a sounder to indicate new faults, this sounder shall have the ability to be muted.

  - Voice Alarm Control Microphone (VACM)

### The VACM shall be EN54 part 16 and BS5839 part 8 compliant. It shall be able to control 8, 16, 24, 32, 40, 48, 56 or 64 zones. It shall be possible to rack mount the control microphone with options for up to 80 zones.

### From the VACM it shall be possible to carry out general paging announcements, either zonal or all call, and select different sources of background music to any zone. By using a key switch it shall be possible to select any/all of the system’s messages that are stored digitally within the AOMs. If the main processor should fail it shall be possible to undertake an emergency ‘all call’ announcement. It shall be possible to adjust zone volume from the control microphone.

### The microphone shall have a red ‘VA active’ LED indicator which illuminates during broadcast of an emergency message or emergency broadcast.

### It shall be possible to fit an emergency processor bypass ‘all call’ switch.

### There shall be a three line LED display for each zone select button which is able to display the zone name, input source and current status of each zone. There shall be an additional LCD display to indicate message choice which shall show four messages at a time and the user shall be able to scroll through all messages available.

### All critical signal paths shall be monitored by using the latest available technology and faults shall be displayed.

### The microphone shall have the ability to be programmed via a USB connection and will have five programmable function keys.

### Fault indicators shall include ‘general’, ‘message’, ‘microphone’, ‘processor’ and ‘data link’. ‘Speak now’ and speech level indicators shall also be a requirement.

### Connection shall be via RJ45/CAT5.

  - Fire Microphone

### The fire microphone shall be EN54 part 16 and BS5839 part 8 compliant. It shall be able to control a single, four or eight zones. From the fire microphone it shall be possible to broadcast a general emergency announcement either on a ‘zonal’ or ‘all call’ basis.

### All connections between the fire microphone and rack installations shall be made in appropriate fire rated cable.

### The units shall be housed within a red coloured sealed robust lockable steel enclosure to be wall or flush mountable. It shall also be possible to mount the unit within a 19” rack.

### The front panel shall have a clear window to allow fault indicators to be seen.

### All critical signal paths shall be monitored by using the latest available technology and faults shall be displayed.

  - Paging Microphone

### The paging microphones shall be aesthetically pleasing and be either desk or wall mountable. They shall be able to control a single zone or 4, 8, 16 or 32 zones. From the paging microphone it shall be possible to carry out general announcements either on a zonal or all call basis.

### Communication with the main control system shall be via an RS485 link with a RJ45 (CAT5 network) cable which will carry both audio and data. The paging microphones shall have the option to be linked together via wall sockets providing the ability to be connected to a single input on the system.

### 4, 8, 16 and 32 zone paging microphones shall have the option to be fully monitored. The paging microphones shall have the following functions: ‘speak now’ light, ‘VA active’ light, ‘limiter’ and ‘zone cancel’ function. There shall also be ‘data’ and ‘power on' indicators to show the unit is functioning correctly.

### The units shall have capabilities to have optional flip top switches fitted to trigger DVA messages.

  - Telephone Interfaces

### The manufacturer of the VACIE shall be capable of supplying telephone interfaces to allow an operator to make a paging call from a telephone as follows:

#### Single zone telephone interface complete with an optional chime.

#### Eight zone store and forward telephone interface complete with optional chime.

  - Amplifiers

### The amplifiers shall be 100 Volt line amplifiers and be supplied in the following power rating options: dual 75 Watt, dual 150 Watt, quad 75 Watt, quad 150 Watt and dual 300 Watt. All amplifiers shall have separate input connectors for all channels.

### The amplifiers shall be Class D and be at least 90% efficient. The amplifiers shall be able to obtain their rated output power from a nominal 24V battery supply.

### The amplifiers shall not contain 100V line transformers for efficiency, size and weight requirements.

### All amplifiers shall incorporate 0dBm balanced line audio inputs.

### The front panel of each amplifier shall have indicators for amplifier output level and amplifier status (‘over temperature’, ‘over load’, ‘mains connected’ and ‘battery connected’).

### The amplifiers shall be mounted into a 19” rack by means of an amplifier mainframe. Each mainframe shall have capabilities to house up to three amplifier modules.

### Each amplifier assembly shall contain its own high efficiency switch mode power supply per two amplifier outputs (except dual 300W which shall incorporate one supply per output) with integrated power factor correction.

### The internal high efficiency switch mode power supplies shall be fully compliant with BS EN54-4:1998 Incorporating Amendments Nos. 1 and 2.

### Each amplifier assembly shall be connected to a charger module to supply up to 2A of battery charging current.

### All fault and status information shall be transmitted to the system.

Dual 75 Watt Amplifier Specification

| 1KHz Rated output power less than 0.2% THD | 75W @ 132 Ohms |
| --- | --- |
| Output regulation | Better than 0.2 dB |
| Output Voltages obtainable | 100V only |
| Frequency response (-3dB) | 35 Hz – 20 kHz |
| Input sensitivity and impedance | 0 dBm @ 10kOhms balanced |
| Input common mode rejection ratio (50Hz – 20kHz) | Better than 40 dB :typically 60 dB |
| Output noise reference to rated output | Better than 80 dB (A) |
| Cross talk between amplifiers at 1Khz | Better than 70dB |
| Supply Voltage (batteries) | 22 – 28V DC |
| Supply current(batteries) standby | 50mA per amplifier |
| Rated output power | 3.75A per amplifier |
| Output stage protection: Thermal Load Action | Output stage above 90 °C Excessive output stage current Reduces input to a safe level using a low distortion VCA |
| Fuse protection AC supply (5 x 20mm) Battery (automotive blade) | 1 x 2A (T) 1 x 20A |
| Terminations: Loudspeaker line output Balanced line inputs DC supply input and paralleling facility | 2 x 2 way cage clamp RJ45 connectors 2 pin crimp connectors |
| Dimensions – mm Weight | W 145 x H 75 x D 310 2.30Kg |
| Mains supply input | IEC 6A filtered connector |
| Mains PSU including power factor correction as part of the amplifier module |  |
| Mains supply | 230 V +10%/-15% 50/60Hz |
| Standby power consumption | 12W |
| Maximum power consumption | 175W |
| Aux DC O/P @ 30V | 2.5A |
| Front panel indicators: Amp status LED Output level LED | AC power, DC power, overload and over temperature 100% yellow / 10% green |

Dual 150 Watt Amplifier Specification

| 1KHz Rated output power less than 0.2% THD | 150W @ 66.6 Ohms |
| --- | --- |
| Output regulation | Better than 0.3 dB |
| Output Voltages obtainable | 100V only |
| Frequency response (-3dB) | 35 Hz – 20 kHz |
| Input sensitivity and impedance | 0dBm @ 10kOhms balanced |
| Input common mode rejection ratio (50Hz – 20kHz) | Better than 40 dB :typically 60 dB |
| Output noise reference to rated output | Better than 80 dB (A) |
| Cross talk between amplifiers at 1Khz | Better than 70dB |
| Supply Voltage (batteries) | 22 – 28V DC |
| Supply current (batteries) standby | 50mA per amplifier |
| Rated output power | 7.5A per amplifier |
| Output stage protection: Thermal Load Action | Output stage above 90 °C Excessive output stage current Reduces input to a safe level using a low distortion VCA |
| Fuse protection AC supply (5 x 20mm) Battery (automotive blade) | 1 x 2A (T) 1 x 20A |
| Terminations: Loudspeaker line output Balanced line inputs DC supply input and paralleling facility | 2 x 2 way cage clamp RJ45 connectors 2 pin crimp connectors |
| Dimensions – mm Weight | W 145 x H 75 x D 310 2.30Kg |
| Mains supply input | IEC 6A filtered connector |
| Mains PSU including power factor correction as part of the amplifier module |  |
| Mains supply | 230 V +10%/-15% 50/60Hz |
| Standby power consumption | 12W |
| Maximum power consumption | 350W |
| Aux DC O/P @ 30V | 2.5A |
| Front panel indicators: Amp status LED Output level LED | AC power, DC power, overload and over temperature 100% yellow / 10% green |

Quad 75 Watt Amplifier Specification

| 1KHz Rated output power less than 0.2% THD | 75W @ 132 Ohms |
| --- | --- |
| Output regulation | Better than 0.2 dB |
| Output Voltages obtainable | 100V only |
| Frequency response (-3dB) | 35 Hz – 20 kHz |
| Input sensitivity and impedance | 0dBm @ 10kOhms balanced |
| Input common mode rejection ratio (50Hz – 20kHz) | Better than 40 dB :typically 60 dB |
| Output noise reference to rated output | Better than 80 dB (A) |
| Cross talk between amplifiers at 1Khz | Better than 70dB |
| Supply Voltage (batteries) | 22 – 28V DC |
| Supply current (batteries) standby | 50mA per amplifier |
| Rated output power | 3.75A per amplifier |
| Output stage protection: Thermal Load Action | Output stage above 90 °C Excessive output stage current Reduces input to a safe level using a low distortion VCA |
| Fuse protection AC supply (5 x 20mm) Battery (automotive blade) | 2 x 2A (T) 2 x 20A |
| Terminations: Loudspeaker line output Balanced line inputs DC supply input and paralleling facility | 4 x 2 way cage clamp RJ45 connectors 2 pin crimp connectors |
| Dimensions – mm Weight | W 145 x H 75 x D 310 3.1Kg |
| Mains supply input | IEC 6A filtered connector |
| Mains PSU including power factor correction as part of the amplifier module |  |
| Mains supply | 230 V +10%/-15% 50/60Hz |
| Standby power consumption | 24W |
| Maximum power consumption | 350W |
| Aux DC O/P @ 30V | 5A |
| Front panel indicators: Amp status LED Output level LED | AC power, DC power, overload and over temperature 100% yellow / 10% green |

Quad 150 Watt Amplifier Specification

| 1KHz Rated output power less than 0.2% THD | 150W @ 66 Ohms |
| --- | --- |
| Output regulation | Better than 0.3 dB |
| Output Voltages obtainable | 100V only |
| Frequency response (-3dB) | 35 Hz – 20 kHz |
| Input sensitivity and impedance | 0dBm @ 10kOhms balanced |
| Input common mode rejection ratio (50Hz – 20kHz) | Better than 40 dB :typically 60 dB |
| Output noise reference to rated output | Better than 80 dB (A) |
| Cross talk between amplifiers at 1Khz | Better than 70dB |
| Supply Voltage (batteries) | 22 – 28V DC |
| Supply current (batteries) standby | 50mA per amplifier |
| Rated output power | 7.5A per amplifier |
| Output stage protection: Thermal Load Action | Output stage above 90 °C Excessive output stage current Reduces input to a safe level using a low distortion VCA |
| Fuse protection AC supply (5 x 20mm) Battery (automotive blade) | 2 x 2A (T) 2 x 20A |
| Terminations: Loudspeaker line output Balanced line inputs DC supply input and paralleling facility | 4 x 2 way cage clamp RJ45 connectors 2 pin crimp connectors |
| Dimensions – mm Weight | W 145 x H 75 x D 310 3.1Kg |
| Mains supply input | IEC 6A filtered connector |
| Mains PSU including power factor correction as part of the amplifier module |  |
| Mains supply | 230 V +10%/-15% 50/60Hz |
| Standby power consumption | 24W |
| Maximum power consumption | 700W |
| Aux DC O/P @ 30V | 5A |
| Front panel indicators: Amp status LED Output level LED | AC power, DC power, overload and over temperature 100% yellow / 10% green |

Dual 300 Watt Amplifier Specification

| 1KHz Rated output power less than 0.2% THD | 300W @ 33.3 Ohms |
| --- | --- |
| Output regulation | Better than 0.5 dB |
| Output Voltages obtainable | 100V only |
| Frequency response (-3dB) | 35 Hz – 20 kHz |
| Input sensitivity and impedance | 0dBm @ 10kOhms balanced |
| Input common mode rejection ratio (50Hz – 20kHz) | Better than 40 dB :typically 60 dB |
| Output noise reference to rated output | Better than 85 dB (A) |
| Cross talk between amplifiers at 1Khz | Better than 70dB |
| Supply Voltage (batteries) | 22 – 28V DC |
| Supply current (batteries) standby | 50mA per amplifier |
| Rated output power | 14A per amplifier |
| Output stage protection: Thermal Load Action | Output stage above 90 °C Excessive output stage current Reduces input to a safe level using a low distortion VCA |
| Fuse protection AC supply (5 x 20mm) Battery (automotive blade) | 2 x 2A (T) 2 x 20A |
| Terminations: Loudspeaker line output Balanced line inputs DC supply input and paralleling facility | 2 x 2 way cage clamp RJ45 connectors 2 pin crimp connectors |
| Dimensions – mm Weight | W 145 x H 75 x D 310 3.1Kg |
| Mains supply input | IEC 6A filtered connector |
| Mains PSU including power factor correction as part of the amplifier module |  |
| Mains supply | 230 V +10%/-15% 50/60Hz |
| Standby power consumption | 24W |
| Maximum power consumption | 700W |
| Aux DC O/P @ 30V | 5A |
| Front panel indicators: Amp status LED Output level LED | AC power, DC power, overload and over temperature 100% yellow / 10% green |

  - Charger Module

### The charger shall be fitted in an amplifier mainframe next to an AOM (giving either: two amplifier modules + charger + AOM; or, three x amplifier modules per mainframe).

### It shall be possible to connect up to five amplifiers to a charger module to give a total battery charging current of 10A.

### The charger module shall provide (with associated sealed lead acid batteries) a minimum of 24 hours of system operation in the quiescent condition followed by 30 minutes at full load.

### The charger module shall be fully compliant with BS EN54-4:1998 Incorporating Amendments Nos. 1 and 2

### The charger module shall be capable of charging a battery discharged to its final voltage to at least 80% of its rated capacity within 24 hours and to its rated capacity within a further 48 hours.

### The power supply in the battery charger is to have a constant voltage output with compensation for variation in battery temperature. The batteries are to be protected from discharge by a solid state switch which disconnects the negative terminal.

### The charger module shall maintain the batteries at float level and in good condition at an ambient temperature of 25 degrees Celsius.

### The charger module shall supply fault and status information to the rest of the system.

Charger module specification

| Voltage @ 20°C | 27.3V |
| --- | --- |
| Temperature compensation | -48m V/°C |
| Maximum current | 10A |
| Battery low fault voltage | 22V |
| Battery high resistance fault | 22m Ohm |
| Battery deep discharge cut off voltage | 18V |
| Volt free fault relay output contacts | 100V @ 1A maximum |
| Front panel indicators |  |
| AC supply | AC supply ‘on’ |
| OK | No fault |
| Fuse | Fuse fault |
| Charger fault | Charger fault |
| High resistance battery | High resistance battery fault |
| Low | Battery voltage low fault |
| Terminations |  |
| 24V battery input | 2 pin screw connector |
| DC output, fault relay contacts and external temperature sensor connection | 8 pin screw connector |
| DC & Data | 5 x RJ45 connectors |

  - Digital Network

    - The VACIE shall have capabilities to form part of a decentralised system and racks shall be linked via a digital network. Cabling between racks shall be as either copper, fibre or both. In each of the control matrices there shall be fitted a network control card that communicates to the rack-fitted CANBUS copper or fibre interface modules.

    - The copper or fibre network shall be connected in a loop configuration to minimise cabling. The system must continue to function if cabling is damaged in a single location.

    - It must be possible for up to 14 concurrent audio channels and shall have two RS485 channels in addition to the audio.

    - Network status indicators are to be provided and the network fully monitored.

    - There shall be an optional system reset feature.

    - Network Control Card

      - It shall be possible to configure the network control cards from the matrix’s control menu.

      - The following connectors shall be provided: optional system reset feature (two pin); connector for clockwise network cable (CAT5 patch lead); connector for anti-clockwise network cable (CAT5 patch lead).

      - Slow speed option shall provide 6 concurrent audio channels with 2xRS485 channels. Fast speed option shall provide 14 concurrent audio channels with 2xRS485 channels.

      - The RS485 channels shall be independently configurable for speed, bits, parity and stop.

    - Digital Network Copper Interface

      - It shall be possible to connect the copper interface to the network control card by CAT5 patch lead, for connection clockwise or anti-clockwise.

      - The copper interface module shall have screw terminals for two transmit conductors (twisted pair recommended). It shall also have screw terminals for two receive conductors (twisted pair recommended) and a screw terminal for ground.

      - It shall be possible to transmit slow speed up to a distance of 300m, or fast speed up to a distance of 200m.

    - Digital Network Fibre Interface

      - It shall be possible to connect the copper interface to the network control card by CAT5 patch lead, for connection clockwise or anti-clockwise.

      - The fibre interface module shall have an ST fibre transmit connector (multi-mode) and a ST fibre receive connector (multi-mode). There shall also be a screw terminal for ground.

      - There shall be fibre modules to connect both Multimode and Single Mode Fibre types with

      - It shall be possible to transmit at either slow or fast speed at a distance up to 3km (multimode) and 4km (single mode).

  - Ambient Noise Sensing (optional)

    - This facility is ideal for any location where audibility could be a problem due to variable noise level, such as Leisure centres, railway stations, shopping malls or factories etc. When the area is at its quietest the volume of the announcements or music will reduce. When the areas are at their busiest and noisiest the amplifiers increase in power to ensure that all announcements etc. will be audible above the background noise.

    - The Ambient Noise Sensing device shall work in conjunction with DSP routeing matrix to automatically adjust the power of the amplifier depending on the ambient noise.

    - The Ambient noise sensor shall contain a dynamic microphone capsule, the output of which shall be amplified then converted to produce a variable current output.

    - The amplifier that is used to convert the signal shall have band pass filters to ensure the system only responds to noise that affects the level of ambient noise.

  - Power supply/standby operation

    - Provide a 24V DC battery support comprising battery and charger. The charger is to form part of the amplifier supply. The battery support is to have sufficient capacity to maintain the system operation for up to 24 hours in a quiescent mode plus 30 minutes at full load. The amplifiers and standby batteries are to be constructed in accordance with clause 4 and 5 of BS5839 part 4 1988. Sealed lead acid batteries shall be utilised.

    - The battery charger is to be capable of re-charging discharged batteries to 100% of their rated capacity within a 24 hour period and >80% within 12 hours.

    - The power supply in the battery charger is to have a constant voltage output with compensation for variation in battery temperature. The batteries are to be protected from discharge by a solid state switch which disconnects the negative terminal.

    - The power supply and supervisory board are to be designed to maintain the batteries on float charge and in good condition at an ambient temperature of 25 degrees C.

    - Provide visual indication of mains status, battery disconnected and charger fail on the power supply module should be indicated as well as on the routeing matrix.

    - Provide a standby amplifier controller module and amplifier to automatically switch in a spare amplifier to replace a failed amplifier and indicate which amplifier has failed.

  - Background music

    - The system shall have capabilities to play different music sources to any combination of zones or zone.

  - Room panels – type 1 – volume control & channel source select

    - It shall be possible to locally control audio facilities via room panels. The finish of the panel shall be stainless steel. The room panel should have the option to be mounted within a protective stainless steel enclosure. The room panel shall enable channel select and volume adjustment to the local zone. (Consultant to provide further information on this.)

  - Room panels – type 2 – audio input panel with volume control

    - It shall be possible to locally control audio facilities via room panels. The finish of the panel shall be stainless steel. The room panel should have the option to be mounted within a protective stainless steel enclosure. The panel shall provide facilities to connect a music source and/or microphone for local broadcast. The panel shall have two phono sockets and 35mm jack socket for input from music source. The panel shall have switches for: on/off priority for microphone and auto fade switch. (Consultant to provide further information on this.)

  - Advert injection

    - The system shall have sufficient inputs to allow for a single advert injection machine.

  - Fire Alarm Interface

    - The system shall have a fire alarm interface to allow triggering from the Fire Detection system. (Consultant to provide further information on this)

  - Interfaces to other equipment

    - The system shall allow for inputs from other equipment. (xxxxxx please provide further information on this)

  - Touchscreen

    - The system shall have capabilities to be controlled be Touchscreen software.

  - Download software

    - The system shall have capabilities to be programmed via laptop computer via a USB port on the front panel of the routeing matrix

  - Remote access and monitoring

    - The system shall have capabilities to allow remote access and monitoring of the system.

  - Loudspeakers

    - The loudspeaker design is the responsibility of the sound system contractor unless otherwise agreed.

    - The supplied loudspeakers shall be compliant with BS5839 part 8 and EN54 part 24.

  - Recommended loudspeakers:

    - HORN – for use in external and industrial environments or environments with high noise levels or in acoustically difficult conditions.

    - FLUSH MOUNTING – for use in offices, department stores and supermarkets.

    - Wall mounted – for use in offices, small workshops, stores and general small areas in buildings.

    - Bi-directional – for use in corridors and long narrow areas.

    - Column having a wide horizontal and narrow vertical coverage angle – for use in halls and concourse areas.

    - PROJECTOR – mounted in a tube fixed by means of an adjustable bracket thus enabling the propagation of sound in a preferred direction.

    - EXPLOSION-PROTECTED (for example flameproof horn) – suitable for use in potentially explosive areas.

- Factory Acceptance Test

  - The manufacturer shall provide a detailed Factory Acceptance Test to be held at their premises.

- System installation

  - The installation of the system is to be carried out by others and the manufacturer of the system shall provide detailed wiring diagrams and operating manuals.

- System Maintenance

  - The manufacturer of the Voice Evacuation system shall be able to maintain the system on a quarterly basis. Maintenance to be carried out must include.

  - Daily – To be completed by the end user

    - The following routine maintenance is to be carried out by a competent person as appointed by the customer.  Baldwin Boxall will allow one hour for refresher training of staff during the annual visit.

    - Check control panel indicators are operating as normal and complete daily log. Report any faults.

    - Check fault records to confirm any outstanding actions.

  - Weekly –  To be completed by the end user

    - The following routine maintenance is to be carried out by a competent person as appointed by the customer.  Baldwin Boxall will allow one hour for refresher training of staff during the annual visit.

    - Test system functionality in conjunction with Fire Alarm System, make subjective assessment of message intelligibility.

    - Test all microphones for correct operation.

    - At least one loudspeaker must be checked weekly, over a 13 week period all loudspeaker zones must be checked.

    - Report and log any faults identified. Complete system test log.

  - Quarterly –  To be carried out by the manufacturer

    - Scheduled attendance by maintenance engineer to carry out inspection of systems.  As a minimum, the following will be checked during the visit:

    - Visual check of batteries and battery connections and electrically test to determine any deterioration.

    - Test Emergency messages and Fire Microphones.

    - Check and record parameters of ‘end line monitors’.

    - Make subjective assessment of message intelligibility and general condition of speakers.

    - Check and test interface connections with premise’s Fire Alarm Panel.

    - Carry out functionality test of system.

    - Review report log and identify/address any outstanding events.

    - Provide refresher training for site appointed staff (six monthlies).

    - Discharge test of battery system.

  - Annually –  To be carried out by the manufacturer

    - Scheduled attendance by maintenance Engineer to carry out inspection of systems and provide Certificate of Compliance to BS5839 Part 8.

    - In addition to those items identified in the quarterly test, the following will be carried out:

    - Visual check of systems and infrastructure wiring.

    - Check the Sound Pressure Level at each loudspeaker zone; confirm that the Emergency Broadcast is at a practical level above the ambient noise.  RASTI tests are not included, we would be pleased to provide quotations for this service.

    - Assess results against previously reported figures, to determine overall system performance.

    - Issue Certificate of Compliance to BS5839 Part 8.

- Tests

# Documentation

  - Issue a system test certificate detailing compliance will the relevant British Standards and this specification.

  - Issue copies of all documentation immediately to the engineer for comment prior to inclusion in the handover documentation.